## Sheet1
Table 1: Government regulations used for the Office Block
Building Element Type | Current Building Standard (2023-2025) | Future Building Standard (2025 onwards)
Roof (flat roof) U-Value W/ | 0.18 | 0.18
.K
Wall U-Value W/ | 0.26 | 0.26
.K
Floor U-Value W/ | 0.18 | 0.18
.K
Windows, roof windows, curtain walling U-Value W/ | 1.6 | 1.6
Pedestrian doors (including glazed doors) U-Value W/ | 1.6 | 1.4
.K
Outdoor air supply to occupiable rooms air flow rate l/s per | 1 | 1.5
Common spaces in offices, such as corridors and lift lobbies air flow rate l/s per | 0.5 | 0.5
Table 2: Yearly consumption (kWh) of the office block model, colour coded in conjunction with the matching KGCC
Location | Heating | Cooling | Other
Aberdeen | 139000 | 7000 | 532000
Brighton | 118000 | 11000 | 525000
Belfast | 125000 | 9000 | 525000
Birmingham | 130000 | 16000 | 527000
Finsingley | 136000 | 14000 | 525000
Hemsby | 118000 | 16000 | 525000
Jersey Channel Islands | 66000 | 21000 | 525000
Lewchas | 146000 | 7000 | 522000
London Gatwick | 118000 | 23000 | 525000
Oban | 107000 | 7000 | 525000
Table 3: Monthly electrical consumption (kWh) of the Office block model in London
Month | Heating | Cooling | Other (Lighting, Equipment, Fans) | Total
Jan | 32217 | 0 | 42297 | 74514
Feb | 26908 | 0 | 40921 | 67829
Mar | 17376 | 0 | 42402 | 59778
Apr | 5671 | 0 | 41754 | 47425
May | 0 | 2896 | 42103 | 44999
Jun | 0 | 5551 | 41212 | 46763
Jul | 0 | 7240 | 42693 | 49933
Aug | 0 | 6275 | 42253 | 48528
Sep | 0 | 9291 | 40634 | 49925
Oct | 7481 | 241 | 41798 | 49520
Nov | 18703 | 0 | 41075 | 59778
Dec | 30287 | 0 | 42179 | 72466
Annual | 138643 | 31494 | 501321 | 671458
Table 4: Hourly electrical consumption of the office model during a summer day in London
Hour | Heating (kWh) |  | Cooling (kWh) | Other Loads (kWh) | Total (kWh)
1:00 | 0 |  | 0 | 0 | 0
2:00 | 0 |  | 0 | 0 | 0
3:00 | 0 |  | 0 | 0 | 0
4:00 | 0 |  | 0 | 0 | 0
5:00 | 0 |  | 0 | 0 | 0
6:00 | 0 |  | 0 | 0 | 0
7:00 | 0 |  | 0 | 40 | 40
8:00 | 0 |  | 0 | 95 | 95
9:00 | 0 |  | 0 | 107 | 107
10:00 | 0 |  | 0 | 109 | 109
11:00 | 0 |  | 0 | 110 | 110
12:00 | 0 |  | 8 | 108 | 116
13:00 | 0 |  | 20 | 108 | 128
14:00 | 0 |  | 35 | 108 | 143
15:00 | 0 |  | 52 | 110 | 162
16:00 |  | 0 | 60 | 110 | 170
17:00 |  | 0 | 64.79 | 110 | 174.79
18:00 |  | 0 | 0 | 67 | 67
19:00 |  | 0 | 0 | 30 | 30
20:00 |  | 0 | 0 | 0 | 0
21:00 |  | 0 | 0 | 0 | 0
22:00 |  | 0 | 0 | 0 | 0
23:00 |  | 0 | 0 | 0 | 0
24:00 |  | 0 | 0 | 0 | 0

## Sheet2
FC_WINTER(Figure 9) | [5 empty] | FC_SUMMER (Figure 6) | [5 empty] | ELECTROLYSER_WINTER (Figure 8) | [5 empty] | ELECTROLYSER_SUMMER (Figure 5) | [5 empty] | Power consumption |  | PV Data |  | H2O consumption and H2O balance (Figure 7a) |  |  | H₂ Consumption and H₂ Balance (Figure 7b)
H2O(Figure 9 a) |  | H2(Figure 9 b) |  | O2(Figure 9 c) |  | H2O(Figure 6 a) |  | H2(Figure 6 b) |  | O2(Figure 6 c) |  | H2O(Figure 8 a) |  | H2(Figure 8 b) |  | O2(Figure 8 c) |  | H2O (Figure 5 a) |  | H2(Figure 5 b) |  | O2(Figure 5 c) |  | summer 01.07 (kwh ) | winter 06.12 (kwh ) | summer 01.07 (kwh) | winter 06.12 (kwh) | Month | H₂O Consumption (t) | H₂O Balance (kg) | Month | H₂ Consumption (kg) | H₂ Balance (kg)
Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) | Time(s) | Flow rate(kg/s) |  |  |  |  | 1 | 4.8 | 6 | 1 | 630 | 750
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.597e-38 | 0 | 0 | 0 | 0 | 0 | -2.5756e-12 | 0 | -4.0215e-87 | 0 | 0 | 0 | -2.5756e-12 | 0 | -4.0215e-87 | 1.7702 | 4.2054 | 3.591 | 3.228 | 2 | 14.2 | 7.1 | 2 | 800 | 440
1.5088e-09 | -1.6398e-10 | 1.5088e-09 | -1.6398e-10 | 1.5088e-09 | -1.1691e-14 | 1.5088e-09 | -1.6398e-10 | 1.5088e-09 | 1.8205e-08 | 1.5088e-09 | -1.1691e-14 | 1.93e-10 | 3.2141e-26 | 1.93e-10 | -2.5756e-12 | 1.93e-10 | -9.7288e-14 | 1.8405e-10 | 2.0433e-26 | 1.8405e-10 | -2.5756e-12 | 1.8405e-10 | -8.3121e-14 | 1.1206 | 4.172 | 3.564 | 3.258 | 3 | 16.2 | 8.2 | 3 | 925 | 440
3.0175e-09 | -3.2759e-10 | 3.0175e-09 | -3.2759e-10 | 3.0175e-09 | -1.2803e-15 | 3.0175e-09 | -3.2759e-10 | 3.0175e-09 | 5.4033e-08 | 3.0175e-09 | -1.2803e-15 | 3.86e-10 | 1.1289e-25 | 3.86e-10 | -2.5756e-12 | 3.86e-10 | -2.3472e-13 | 3.6809e-10 | 8.5636e-26 | 3.6809e-10 | -2.5756e-12 | 3.6809e-10 | -2.4419e-13 | 1.1206 | 3.7015 | 3.651 | 3.36 | 4 | 15.5 | 8 | 4 | 890 | 438
1.05e-08 | -1.1299e-09 | 1.05e-08 | -1.1299e-09 | 1.05e-08 | 2.8175e-12 | 1.05e-08 | -1.1299e-09 | 1.05e-08 | 6.0459e-07 | 1.05e-08 | 2.8175e-12 | 6.2519e-10 | 3.262e-25 | 6.2519e-10 | -2.5756e-12 | 6.2519e-10 | -5.2675e-13 | 5.9698e-10 | 2.616e-25 | 5.9698e-10 | -2.5756e-12 | 5.9698e-10 | -4.9875e-13 | 1.1206 | 3.6578 | 3.72 | 3.384 | 5 | 16.1 | 8.3 | 5 | 925 | 438
1.9077e-08 | -2.038e-09 | 1.9077e-08 | -2.038e-09 | 1.9077e-08 | 1.341e-11 | 1.9077e-08 | -2.038e-09 | 1.9077e-08 | 1.6494e-06 | 1.9077e-08 | 1.341e-11 | 9.2283e-10 | 8.0551e-25 | 9.2283e-10 | -2.5756e-12 | 9.2283e-10 | -8.8671e-13 | 8.8063e-10 | 6.811e-25 | 8.8063e-10 | -2.5756e-12 | 8.8063e-10 | -8.9364e-13 | 1.1206 | 3.598 | 3.579 | 3.297 | 6 | 15.5 | 8 | 6 | 890 | 438
2.8508e-08 | -3.0269e-09 | 2.8508e-08 | -3.0269e-09 | 2.8508e-08 | 3.3034e-11 | 2.8508e-08 | -3.0269e-09 | 2.8508e-08 | 3.105e-06 | 2.8508e-08 | 3.3034e-11 | 1.2938e-09 | 1.6626e-24 | 1.2938e-09 | -2.5756e-12 | 1.2938e-09 | -1.4239e-12 | 1.2327e-09 | 1.4523e-24 | 1.2327e-09 | -2.5756e-12 | 1.2327e-09 | -1.4061e-12 | 1.1206 | 3.6894 | 4.323 | 3.357 | 7 | 16.2 | 8.3 | 7 | 925 | 440
4.3906e-08 | -4.6148e-09 | 4.3906e-08 | -4.6148e-09 | 4.3906e-08 | 9.7101e-11 | 4.3906e-08 | -4.6148e-09 | 4.3906e-08 | 6.1915e-06 | 4.3906e-08 | 9.7101e-11 | 1.8043e-09 | 3.4912e-24 | 1.8043e-09 | -2.5756e-12 | 1.8043e-09 | -2.4067e-12 | 1.7202e-09 | 3.1439e-24 | 1.7202e-09 | -2.5756e-12 | 1.7202e-09 | -2.39e-12 | 1.1206 | 6.1893 | 4.155 | 3.444 | 8 | 16.2 | 8.3 | 8 | 925 | 440
8.4779e-08 | -8.6658e-09 | 8.4779e-08 | -8.6658e-09 | 8.4779e-08 | 6.0569e-10 | 8.4779e-08 | -8.6658e-09 | 8.4779e-08 | 1.7385e-05 | 8.4779e-08 | 6.0569e-10 | 2.7191e-09 | 9.1811e-24 | 2.7191e-09 | -2.5756e-12 | 2.7191e-09 | -4.2613e-12 | 2.5996e-09 | 8.5139e-24 | 2.5996e-09 | -2.5756e-12 | 2.5996e-09 | -4.3107e-12 | 1.6631 | 7.2615 | 17.25 | 3.357 | 9 | 15.5 | 8 | 9 | 890 | 438
1.1591e-07 | -1.1598e-08 | 1.1591e-07 | -1.1598e-08 | 1.1591e-07 | 1.397e-09 | 1.1591e-07 | -1.1598e-08 | 1.1591e-07 | 2.8041e-05 | 1.1591e-07 | 1.397e-09 | 3.8193e-09 | 2.0806e-23 | 3.8193e-09 | -2.5756e-12 | 3.8193e-09 | -6.9773e-12 | 3.6497e-09 | 1.941e-23 | 3.6497e-09 | -2.5756e-12 | 3.6497e-09 | -6.8788e-12 | 1.8773 | 7.5304 | 12.657 | 3.354 | 10 | 16.1 | 8.3 | 10 | 925 | 438
1.4704e-07 | -1.4407e-08 | 1.4704e-07 | -1.4407e-08 | 1.4704e-07 | 2.6513e-09 | 1.4704e-07 | -1.4407e-08 | 1.4704e-07 | 3.9594e-05 | 1.4704e-07 | 2.6513e-09 | 4.9875e-09 | 3.9563e-23 | 4.9875e-09 | -2.5756e-12 | 4.9875e-09 | -9.9615e-12 | 4.7607e-09 | 3.6868e-23 | 4.7607e-09 | -2.5756e-12 | 4.7607e-09 | -9.8271e-12 | 1.8773 | 7.4682 | 20.463 | 12.381 | 11 | 15.5 | 8 | 11 | 890 | 438
1.7817e-07 | -1.7101e-08 | 1.7817e-07 | -1.7101e-08 | 1.7817e-07 | 4.4393e-09 | 1.7817e-07 | -1.7101e-08 | 1.7817e-07 | 5.164e-05 | 1.7817e-07 | 4.4393e-09 | 6.3343e-09 | 6.9993e-23 | 6.3343e-09 | -2.5756e-12 | 6.3343e-09 | -1.3283e-11 | 6.0442e-09 | 6.5255e-23 | 6.0442e-09 | -2.5756e-12 | 6.0442e-09 | -1.3129e-11 | 1.9844 | 7.5915 | 27.657 | 18.417 | 12 | 16.1 | 8.3 | 12 | 925 | 440
2.1882e-07 | -2.0458e-08 | 2.1882e-07 | -2.0458e-08 | 2.1882e-07 | 7.6591e-09 | 2.1882e-07 | -2.0458e-08 | 2.1882e-07 | 6.7805e-05 | 2.1882e-07 | 7.6591e-09 | 8.0286e-09 | 1.2217e-22 | 8.0286e-09 | -2.5756e-12 | 8.0286e-09 | -1.7337e-11 | 7.6622e-09 | 1.1417e-22 | 7.6622e-09 | -2.5756e-12 | 7.6622e-09 | -1.7133e-11 | 1.6227 | 5.1649 | 36.501 | 22.791
2.7721e-07 | -2.4997e-08 | 2.7721e-07 | -2.4997e-08 | 2.7721e-07 | 1.4134e-08 | 2.7721e-07 | -2.4997e-08 | 2.7721e-07 | 9.1627e-05 | 2.7721e-07 | 1.4134e-08 | 1.0213e-08 | 2.1279e-22 | 1.0213e-08 | -2.5756e-12 | 1.0213e-08 | -2.2093e-11 | 9.7343e-09 | 1.9875e-22 | 9.7343e-09 | -2.5756e-12 | 9.7343e-09 | -2.1796e-11 | 1.6227 | 4.7954 | 34.314 | 25.749
3.1245e-07 | -2.7583e-08 | 3.1245e-07 | -2.7583e-08 | 3.1245e-07 | 1.911e-08 | 3.1245e-07 | -2.7583e-08 | 3.1245e-07 | 0.00010606 | 3.1245e-07 | 1.911e-08 | 1.3059e-08 | 3.7066e-22 | 1.3059e-08 | -2.5756e-12 | 1.3059e-08 | -2.7326e-11 | 1.2393e-08 | 3.4371e-22 | 1.2393e-08 | -2.5756e-12 | 1.2393e-08 | -2.695e-11 | 1.6227 | 4.7894 | 20.682 | 26.364
3.3056e-07 | -2.8871e-08 | 3.3056e-07 | -2.8871e-08 | 3.3056e-07 | 2.1982e-08 | 3.3056e-07 | -2.8871e-08 | 3.3056e-07 | 0.00011317 | 3.3056e-07 | 2.1982e-08 | 1.695e-08 | 6.596e-22 | 1.695e-08 | -2.5756e-12 | 1.695e-08 | -3.2592e-11 | 1.5953e-08 | 6.0255e-22 | 1.5953e-08 | -2.5756e-12 | 1.5953e-08 | -3.2062e-11 | 1.6227 | 4.6516 | 36.024 | 22.065
3.4866e-07 | -3.0134e-08 | 3.4866e-07 | -3.0134e-08 | 3.4866e-07 | 2.5066e-08 | 3.4866e-07 | -3.0134e-08 | 3.4866e-07 | 0.00011981 | 3.4866e-07 | 2.5067e-08 | 2.279e-08 | 1.252e-21 | 2.279e-08 | -2.5756e-12 | 2.279e-08 | -3.6586e-11 | 2.1169e-08 | 1.1155e-21 | 2.1169e-08 | -2.5756e-12 | 2.1169e-08 | -3.5998e-11 | 1.6227 | 4.9544 | 32.976 | 6.066
3.6677e-07 | -3.1371e-08 | 3.6677e-07 | -3.1371e-08 | 3.6677e-07 | 2.8358e-08 | 3.6677e-07 | -3.1371e-08 | 3.6677e-07 | 0.00012592 | 3.6677e-07 | 2.8359e-08 | 3.2871e-08 | 2.7222e-21 | 3.2871e-08 | -2.5756e-12 | 3.2871e-08 | -3.2216e-11 | 2.9888e-08 | 2.3281e-21 | 2.9888e-08 | -2.5756e-12 | 2.9888e-08 | -3.3246e-11 | 1.6227 | 5.0424 | 28.245 | 5.07
3.9474e-07 | -3.3237e-08 | 3.9474e-07 | -3.3237e-08 | 3.9474e-07 | 3.3841e-08 | 3.9465e-07 | -3.3231e-08 | 3.9465e-07 | 0.00013437 | 3.9465e-07 | 3.3824e-08 | 5.407e-08 | 7.6626e-21 | 5.407e-08 | -2.5757e-12 | 5.407e-08 | 2.3244e-11 | 4.7404e-08 | 6.1072e-21 | 4.7404e-08 | -2.5756e-12 | 4.7404e-08 | 7.8953e-12 | 2.1652 | 5.1682 | 17.328 | 3.237
4.3232e-07 | -3.5659e-08 | 4.3232e-07 | -3.5659e-08 | 4.3232e-07 | 4.1938e-08 | 4.3237e-07 | -3.5663e-08 | 4.3237e-07 | 0.00014424 | 4.3237e-07 | 4.1949e-08 | 1.083e-07 | 3.1704e-20 | 1.083e-07 | -2.5757e-12 | 1.083e-07 | 4.4846e-10 | 9.0887e-08 | 2.3244e-20 | 9.0887e-08 | -2.5757e-12 | 9.0887e-08 | 3.1388e-10 | 2.1652 | 5.5301 | 14.175 | 3.258
4.7384e-07 | -3.8232e-08 | 4.7384e-07 | -3.8232e-08 | 4.7384e-07 | 5.1807e-08 | 4.7008e-07 | -3.8003e-08 | 4.7008e-07 | 0.00015271 | 4.7008e-07 | 5.0877e-08 | 1.8993e-07 | 9.8831e-20 | 1.8993e-07 | -2.5757e-12 | 1.8993e-07 | 1.8482e-09 | 1.661e-07 | 7.899e-20 | 1.661e-07 | -2.5757e-12 | 1.661e-07 | 1.5216e-09 | 2.1652 | 11.3616 | 5.391 | 3.225
5.1536e-07 | -4.0704e-08 | 5.1536e-07 | -4.0704e-08 | 5.1536e-07 | 6.2578e-08 | 5.1428e-07 | -4.0641e-08 | 5.1428e-07 | 0.00016136 | 5.1428e-07 | 6.2286e-08 | 2.8645e-07 | 2.2615e-19 | 2.8645e-07 | -2.5758e-12 | 2.8645e-07 | 4.6617e-09 | 2.5827e-07 | 1.9244e-19 | 2.5827e-07 | -2.5758e-12 | 2.5827e-07 | 4.1575e-09 | 2.1652 | 8.7069 | 23.412 | 3.204
5.6652e-07 | -4.3624e-08 | 5.6652e-07 | -4.3624e-08 | 5.6652e-07 | 7.697e-08 | 5.6747e-07 | -4.3677e-08 | 5.6747e-07 | 0.00017049 | 5.6747e-07 | 7.7245e-08 | 4.1892e-07 | 4.8551e-19 | 4.1892e-07 | -2.5759e-12 | 4.1892e-07 | 1.0517e-08 | 3.7778e-07 | 4.1352e-19 | 3.7778e-07 | -2.5758e-12 | 3.7778e-07 | 9.4284e-09 | 2.1652 | 8.4018 | 4.395 | 3.246
6.2823e-07 | -4.6978e-08 | 6.2823e-07 | -4.6978e-08 | 6.2823e-07 | 9.5776e-08 | 6.2919e-07 | -4.7029e-08 | 6.2919e-07 | 0.00017981 | 6.2919e-07 | 9.6078e-08 | 6.4168e-07 | 1.1423e-18 | 6.4168e-07 | -2.576e-12 | 6.4168e-07 | 2.537e-08 | 5.7014e-07 | 9.4483e-19 | 5.7014e-07 | -2.576e-12 | 5.7014e-07 | 2.2161e-08 | 2.1652 | 8.7675 | 4.533 | 3.189
6.8994e-07 | -5.0168e-08 | 6.8994e-07 | -5.0168e-08 | 6.8994e-07 | 1.1594e-07 | 7.0118e-07 | -5.0734e-08 | 7.0118e-07 | 0.00018944 | 7.0118e-07 | 1.1972e-07 | 9.9113e-07 | 2.7305e-18 | 9.9113e-07 | -2.5763e-12 | 9.9113e-07 | 6.0628e-08 | 8.8229e-07 | 2.2677e-18 | 8.8229e-07 | -2.5763e-12 | 8.8229e-07 | 5.3424e-08 | 1.7702 | 9.4731 | 4.302 | 3.204
7.7148e-07 | -5.4163e-08 | 7.7148e-07 | -5.4163e-08 | 7.7148e-07 | 1.4421e-07 | 7.8685e-07 | -5.4892e-08 | 7.8685e-07 | 0.00019963 | 7.8685e-07 | 1.4969e-07 | 1.4811e-06 | 6.1049e-18 | 1.4811e-06 | -2.5768e-12 | 1.4811e-06 | 1.326e-07 | 1.3308e-06 | 5.1667e-18 | 1.3308e-06 | -2.5767e-12 | 1.3308e-06 | 1.1958e-07
8.756e-07 | -5.8951e-08 | 8.756e-07 | -5.8951e-08 | 8.756e-07 | 1.8223e-07 | 8.8945e-07 | -5.9564e-08 | 8.8945e-07 | 0.00021051 | 8.8945e-07 | 1.8741e-07 | 2.1599e-06 | 1.2992e-17 | 2.1599e-06 | -2.5775e-12 | 2.1599e-06 | 2.6964e-07 | 1.9498e-06 | 1.11e-17 | 1.9498e-06 | -2.5773e-12 | 1.9498e-06 | 2.4685e-07
9.9763e-07 | -6.4183e-08 | 9.9763e-07 | -6.4183e-08 | 9.9763e-07 | 2.2841e-07 | 1.0099e-06 | -6.4688e-08 | 1.0099e-06 | 0.000222 | 1.0099e-06 | 2.3312e-07 | 3.1353e-06 | 2.7394e-17 | 3.1353e-06 | -2.5785e-12 | 3.1353e-06 | 5.2218e-07 | 2.829e-06 | 2.3384e-17 | 2.829e-06 | -2.5782e-12 | 2.829e-06 | 4.8226e-07
1.1249e-06 | -6.9274e-08 | 1.1249e-06 | -6.9274e-08 | 1.1249e-06 | 2.7721e-07 | 1.1369e-06 | -6.9738e-08 | 1.1369e-06 | 0.00023314 | 1.1369e-06 | 2.8182e-07 | 4.5725e-06 | 5.8288e-17 | 4.5725e-06 | -2.58e-12 | 4.5725e-06 | 9.474e-07 | 4.1144e-06 | 4.9485e-17 | 4.1144e-06 | -2.5796e-12 | 4.1144e-06 | 8.8453e-07
1.2527e-06 | -7.4075e-08 | 1.2527e-06 | -7.4075e-08 | 1.2527e-06 | 3.2579e-07 | 1.2658e-06 | -7.4549e-08 | 1.2658e-06 | 0.00024393 | 1.2658e-06 | 3.3069e-07 | 6.744e-06 | 1.2684e-16 | 6.744e-06 | -2.5823e-12 | 6.744e-06 | 1.5617e-06 | 6.0315e-06 | 1.0638e-16 | 6.0315e-06 | -2.5817e-12 | 6.0315e-06 | 1.4772e-06
1.3852e-06 | -7.8769e-08 | 1.3852e-06 | -7.8769e-08 | 1.3852e-06 | 3.7476e-07 | 1.3996e-06 | -7.9264e-08 | 1.3996e-06 | 0.00025521 | 1.3996e-06 | 3.7997e-07 | 9.6776e-06 | 2.6128e-16 | 9.6776e-06 | -2.5855e-12 | 9.6776e-06 | 2.3027e-06 | 8.7714e-06 | 2.2506e-16 | 8.7714e-06 | -2.5846e-12 | 8.7714e-06 | 2.2299e-06
1.5177e-06 | -8.3217e-08 | 1.5177e-06 | -8.3217e-08 | 1.5177e-06 | 4.2173e-07 | 1.5334e-06 | -8.3733e-08 | 1.5334e-06 | 0.00026767 | 1.5334e-06 | 4.2717e-07 | 1.2957e-05 | 4.6845e-16 | 1.2957e-05 | -2.5889e-12 | 1.2957e-05 | 2.9982e-06 | 1.1511e-05 | 3.8771e-16 | 1.1511e-05 | -2.5875e-12 | 1.1511e-05 | 2.8805e-06
1.6501e-06 | -8.7452e-08 | 1.6501e-06 | -8.7452e-08 | 1.6501e-06 | 4.6631e-07 | 1.6673e-06 | -8.7985e-08 | 1.6673e-06 | 0.00028109 | 1.6673e-06 | 4.7189e-07 | 1.6594e-05 | 7.6851e-16 | 1.6594e-05 | -2.5928e-12 | 1.6594e-05 | 3.643e-06 | 1.4741e-05 | 6.3588e-16 | 1.4741e-05 | -2.591e-12 | 1.4741e-05 | 3.5273e-06
1.7849e-06 | -9.1564e-08 | 1.7849e-06 | -9.1564e-08 | 1.7849e-06 | 5.0898e-07 | 1.8011e-06 | -9.2045e-08 | 1.8011e-06 | 0.00029457 | 1.8011e-06 | 5.1391e-07 | 2.0957e-05 | 1.2258e-15 | 2.0957e-05 | -2.5974e-12 | 2.0957e-05 | 4.3082e-06 | 1.8686e-05 | 1.022e-15 | 1.8686e-05 | -2.5952e-12 | 1.8686e-05 | 4.2053e-06
1.9197e-06 | -9.5498e-08 | 1.9197e-06 | -9.5498e-08 | 1.9197e-06 | 5.4884e-07 | 1.9349e-06 | -9.593e-08 | 1.9349e-06 | 0.00030771 | 1.9349e-06 | 5.5315e-07 | 2.6675e-05 | 1.9863e-15 | 2.6675e-05 | -2.6034e-12 | 2.6675e-05 | 5.0562e-06 | 2.3721e-05 | 1.6471e-15 | 2.3721e-05 | -2.6006e-12 | 2.3721e-05 | 4.9494e-06
2.0943e-06 | -1.0035e-07 | 2.0943e-06 | -1.0035e-07 | 2.0943e-06 | 5.9629e-07 | 2.1195e-06 | -1.0103e-07 | 2.1195e-06 | 0.00032521 | 2.1195e-06 | 6.0276e-07 | 3.4706e-05 | 3.3628e-15 | 3.4706e-05 | -2.6119e-12 | 3.4706e-05 | 5.9493e-06 | 3.0404e-05 | 2.7064e-15 | 3.0404e-05 | -2.6078e-12 | 3.0404e-05 | 5.7945e-06
2.3379e-06 | -1.0671e-07 | 2.3379e-06 | -1.0671e-07 | 2.3379e-06 | 6.5505e-07 | 2.3709e-06 | -1.0754e-07 | 2.3709e-06 | 0.00034804 | 2.3709e-06 | 6.6239e-07 | 4.6732e-05 | 6.0976e-15 | 4.6732e-05 | -2.6247e-12 | 4.6732e-05 | 7.0734e-06 | 3.9759e-05 | 4.6283e-15 | 3.9759e-05 | -2.6179e-12 | 3.9759e-05 | 6.8006e-06
2.6508e-06 | -1.1425e-07 | 2.6508e-06 | -1.1425e-07 | 2.6508e-06 | 7.1893e-07 | 2.694e-06 | -1.1523e-07 | 2.694e-06 | 0.00037579 | 2.694e-06 | 7.2681e-07 | 6.6409e-05 | 1.2314e-14 | 6.6409e-05 | -2.6455e-12 | 6.6409e-05 | 8.6035e-06 | 5.3997e-05 | 8.5375e-15 | 5.3997e-05 | -2.6332e-12 | 5.3997e-05 | 8.0954e-06
3.0639e-06 | -1.2323e-07 | 3.0639e-06 | -1.2323e-07 | 3.0639e-06 | 7.8622e-07 | 3.1187e-06 | -1.2434e-07 | 3.1187e-06 | 0.00040993 | 3.1187e-06 | 7.9389e-07 | 0.00010402 | 3.0212e-14 | 0.00010402 | -2.6856e-12 | 0.00010402 | 1.0911e-05 | 7.8848e-05 | 1.8206e-14 | 7.8848e-05 | -2.6599e-12 | 7.8848e-05 | 9.9443e-06
3.6517e-06 | -1.3437e-07 | 3.6517e-06 | -1.3437e-07 | 3.6517e-06 | 8.5612e-07 | 3.7226e-06 | -1.356e-07 | 3.7226e-06 | 0.00045473 | 3.7226e-06 | 8.6286e-07 | 0.00020042 | 1.1216e-13 | 0.00020042 | -2.7897e-12 | 0.00020042 | 1.5249e-05 | 0.00013353 | 5.2214e-14 | 0.00013353 | -2.7192e-12 | 0.00013353 | 1.3097e-05
4.3569e-06 | -1.4558e-07 | 4.3569e-06 | -1.4558e-07 | 4.3569e-06 | 9.1104e-07 | 4.4395e-06 | -1.4676e-07 | 4.4395e-06 | 0.00050341 | 4.4395e-06 | 9.1593e-07 | 0.00035658 | 3.55e-13 | 0.00035658 | -2.9656e-12 | 0.00035658 | 2.0294e-05 | 0.0002521 | 1.861e-13 | 0.0002521 | -2.8507e-12 | 0.0002521 | 1.8021e-05
5.1062e-06 | -1.5534e-07 | 5.1062e-06 | -1.5534e-07 | 5.1062e-06 | 9.4657e-07 | 5.1565e-06 | -1.5592e-07 | 5.1565e-06 | 0.00054825 | 5.1565e-06 | 9.4823e-07 | 0.00056248 | 8.8317e-13 | 0.00056248 | -3.215e-12 | 0.00056248 | 2.5322e-05 | 0.00042699 | 5.3381e-13 | 0.00042699 | -3.0557e-12 | 0.00042699 | 2.3369e-05
5.8555e-06 | -1.6329e-07 | 5.8555e-06 | -1.6329e-07 | 5.8555e-06 | 9.6773e-07 | 5.9258e-06 | -1.6395e-07 | 5.9258e-06 | 0.00059297 | 5.9258e-06 | 9.6919e-07 | 0.00086326 | 2.0797e-12 | 0.00086326 | -3.6091e-12 | 0.00086326 | 3.1057e-05 | 0.00065888 | 1.2708e-12 | 0.00065888 | -3.3505e-12 | 0.00065888 | 2.8803e-05
6.7082e-06 | -1.7056e-07 | 6.7082e-06 | -1.7056e-07 | 6.7082e-06 | 9.821e-07 | 6.8074e-06 | -1.7131e-07 | 6.8074e-06 | 0.0006407 | 6.8074e-06 | 9.8335e-07 | 0.0013692 | 5.2293e-12 | 0.0013692 | -4.2192e-12 | 0.0013692 | 3.8551e-05 | 0.0010175 | 3.0296e-12 | 0.0010175 | -3.8308e-12 | 0.0010175 | 3.542e-05
7.7719e-06 | -1.7759e-07 | 7.7719e-06 | -1.7759e-07 | 7.7719e-06 | 9.9236e-07 | 7.9006e-06 | -1.7831e-07 | 7.9006e-06 | 0.00069562 | 7.9006e-06 | 9.9327e-07 | 0.0021675 | 1.3095e-11 | 0.0021675 | -4.7387e-12 | 0.0021675 | 4.7613e-05 | 0.0016094 | 7.5754e-12 | 0.0016094 | -4.4397e-12 | 0.0016094 | 4.3894e-05
9.096e-06 | -1.8395e-07 | 9.096e-06 | -1.8395e-07 | 9.096e-06 | 9.9943e-07 | 9.2402e-06 | -1.8451e-07 | 9.2402e-06 | 0.00075751 | 9.2402e-06 | 9.9999e-07 | 0.0033099 | 3.0505e-11 | 0.0033099 | -5.2384e-12 | 0.0033099 | 5.7518e-05 | 0.0025128 | 1.8452e-11 | 0.0025128 | -4.9179e-12 | 0.0025128 | 5.3813e-05
1.0756e-05 | -1.8929e-07 | 1.0756e-05 | -1.8929e-07 | 1.0756e-05 | 1.0049e-06 | 1.0931e-05 | -1.8973e-07 | 1.0931e-05 | 0.00082887 | 1.0931e-05 | 1.0054e-06 | 0.0047948 | 6.3933e-11 | 0.0047948 | -5.7644e-12 | 0.0047948 | 6.7554e-05 | 0.0037919 | 4.1968e-11 | 0.0037919 | -5.4404e-12 | 0.0037919 | 6.4633e-05
1.2416e-05 | -1.9264e-07 | 1.2416e-05 | -1.9264e-07 | 1.2416e-05 | 1.0093e-06 | 1.2622e-05 | -1.9296e-07 | 1.2622e-05 | 0.00089439 | 1.2622e-05 | 1.0098e-06 | 0.0065782 | 1.2015e-10 | 0.0065782 | -6.288e-12 | 0.0065782 | 7.7146e-05 | 0.0053605 | 8.376e-11 | 0.0053605 | -5.9634e-12 | 0.0053605 | 7.5081e-05
1.4147e-05 | -1.9479e-07 | 1.4147e-05 | -1.9479e-07 | 1.4147e-05 | 1.0139e-06 | 1.4379e-05 | -1.9501e-07 | 1.4379e-05 | 0.00095757 | 1.4379e-05 | 1.0145e-06 | 0.0086845 | 2.0904e-10 | 0.0086845 | -6.8106e-12 | 0.0086845 | 8.635e-05 | 0.0072089 | 1.5124e-10 | 0.0072089 | -6.4792e-12 | 0.0072089 | 8.5023e-05
1.6239e-05 | -1.9633e-07 | 1.6239e-05 | -1.9633e-07 | 1.6239e-05 | 1.0199e-06 | 1.6524e-05 | -1.9647e-07 | 1.6524e-05 | 0.0010291 | 1.6524e-05 | 1.0207e-06 | 0.011169 | 3.4504e-10 | 0.011169 | -7.3377e-12 | 0.011169 | 9.5285e-05 | 0.0093904 | 2.5615e-10 | 0.0093904 | -6.9973e-12 | 0.0093904 | 9.4674e-05
1.9071e-05 | -1.9738e-07 | 1.9071e-05 | -1.9738e-07 | 1.9071e-05 | 1.0283e-06 | 1.9421e-05 | -1.9746e-07 | 1.9421e-05 | 0.0011179 | 1.9421e-05 | 1.0293e-06 | 0.014073 | 5.4642e-10 | 0.014073 | -7.8682e-12 | 0.014073 | 0.00010394 | 0.011962 | 4.1475e-10 | 0.011962 | -7.5218e-12 | 0.011962 | 0.00010412
2.2451e-05 | -1.9786e-07 | 2.2451e-05 | -1.9786e-07 | 2.2451e-05 | 1.0386e-06 | 2.2853e-05 | -1.9788e-07 | 2.2853e-05 | 0.001214 | 2.2853e-05 | 1.0398e-06 | 0.017408 | 8.3372e-10 | 0.017408 | -8.3952e-12 | 0.017408 | 0.00011222 | 0.014948 | 6.4599e-10 | 0.014948 | -8.0477e-12 | 0.014948 | 0.00011329
2.6131e-05 | -1.9796e-07 | 2.6131e-05 | -1.9796e-07 | 2.6131e-05 | 1.0499e-06 | 2.6586e-05 | -1.9796e-07 | 2.6586e-05 | 0.0013097 | 2.6586e-05 | 1.0514e-06 | 0.021178 | 1.2299e-09 | 0.021178 | -8.9122e-12 | 0.021178 | 0.00012005 | 0.01835 | 9.7062e-10 | 0.01835 | -8.5671e-12 | 0.01835 | 0.00012207
2.981e-05 | -1.9792e-07 | 2.981e-05 | -1.9792e-07 | 2.981e-05 | 1.0614e-06 | 3.0319e-05 | -1.9792e-07 | 3.0319e-05 | 0.001398 | 3.0319e-05 | 1.0629e-06 | 0.025393 | 1.7618e-09 | 0.025393 | -9.415e-12 | 0.025393 | 0.00012739 | 0.02217 | 1.4122e-09 | 0.02217 | -9.0744e-12 | 0.02217 | 0.00013039
3.4569e-05 | -1.9783e-07 | 3.4569e-05 | -1.9783e-07 | 3.4569e-05 | 1.0761e-06 | 3.5187e-05 | -1.9782e-07 | 3.5187e-05 | 0.001503 | 3.5187e-05 | 1.078e-06 | 0.030073 | 2.4612e-09 | 0.030073 | -9.9009e-12 | 0.030073 | 0.00013425 | 0.026422 | 1.9984e-09 | 0.026422 | -9.5663e-12 | 0.026422 | 0.00013823
4.0952e-05 | -1.9769e-07 | 4.0952e-05 | -1.9769e-07 | 4.0952e-05 | 1.0959e-06 | 4.17e-05 | -1.9767e-07 | 4.17e-05 | 0.0016296 | 4.17e-05 | 1.0983e-06 | 0.035271 | 3.3701e-09 | 0.035271 | -1.037e-11 | 0.035271 | 0.00014066 | 0.031245 | 2.783e-09 | 0.031245 | -1.0052e-11 | 0.031245 | 0.00014577
4.8231e-05 | -1.9752e-07 | 4.8231e-05 | -1.9752e-07 | 4.8231e-05 | 1.1185e-06 | 4.8553e-05 | -1.9752e-07 | 4.8553e-05 | 0.0017497 | 4.8553e-05 | 1.1195e-06 | 0.041173 | 4.5689e-09 | 0.041173 | -1.0832e-11 | 0.041173 | 0.00014675 | 0.036786 | 3.8392e-09 | 0.036786 | -1.0535e-11 | 0.036786 | 0.00015308
5.5509e-05 | -1.9736e-07 | 5.5509e-05 | -1.9736e-07 | 5.5509e-05 | 1.1411e-06 | 5.5405e-05 | -1.9736e-07 | 5.5405e-05 | 0.0018589 | 5.5405e-05 | 1.1408e-06 | 0.047876 | 6.1416e-09 | 0.047876 | -1.1285e-11 | 0.047876 | 0.00015251 | 0.043111 | 5.2437e-09 | 0.043111 | -1.1008e-11 | 0.043111 | 0.00016008
6.4422e-05 | -1.9715e-07 | 6.4422e-05 | -1.9715e-07 | 6.4422e-05 | 1.1688e-06 | 6.4575e-05 | -1.9715e-07 | 6.4575e-05 | 0.0019915 | 6.4575e-05 | 1.1693e-06 | 0.055417 | 8.174e-09 | 0.055417 | -1.1725e-11 | 0.055417 | 0.00015786 | 0.05025 | 7.0797e-09 | 0.05025 | -1.1467e-11 | 0.05025 | 0.00016666
7.5844e-05 | -1.9689e-07 | 7.5844e-05 | -1.9689e-07 | 7.5844e-05 | 1.2043e-06 | 7.6403e-05 | -1.9687e-07 | 7.6403e-05 | 0.0021439 | 7.6403e-05 | 1.206e-06 | 0.063833 | 1.0765e-08 | 0.063833 | -1.2159e-11 | 0.063833 | 0.00016273 | 0.058254 | 9.4476e-09 | 0.058254 | -1.1912e-11 | 0.058254 | 0.00017276
8.8898e-05 | -1.9658e-07 | 8.8898e-05 | -1.9658e-07 | 8.8898e-05 | 1.2448e-06 | 8.9522e-05 | -1.9657e-07 | 8.9522e-05 | 0.0022937 | 8.9522e-05 | 1.2468e-06 | 0.073195 | 1.4036e-08 | 0.073195 | -1.2613e-11 | 0.073195 | 0.00016712 | 0.067199 | 1.2472e-08 | 0.067199 | -1.2359e-11 | 0.067199 | 0.00017836
0.00010343 | -1.9625e-07 | 0.00010343 | -1.9625e-07 | 0.00010343 | 1.2899e-06 | 0.00010395 | -1.9624e-07 | 0.00010395 | 0.0024399 | 0.00010395 | 1.2916e-06 | 0.083599 | 1.814e-08 | 0.083599 | -1.3155e-11 | 0.083599 | 0.00017101 | 0.077178 | 1.6305e-08 | 0.077178 | -1.2851e-11 | 0.077178 | 0.00018343
0.00011796 | -1.9591e-07 | 0.00011796 | -1.9591e-07 | 0.00011796 | 1.335e-06 | 0.00011838 | -1.959e-07 | 0.00011838 | 0.0025705 | 0.00011838 | 1.3364e-06 | 0.095156 | 2.3257e-08 | 0.095156 | -1.3932e-11 | 0.095156 | 0.00017442 | 0.088289 | 2.1126e-08 | 0.088289 | -1.3498e-11 | 0.088289 | 0.00018797
0.0001367 | -1.9548e-07 | 0.0001367 | -1.9548e-07 | 0.0001367 | 1.3932e-06 | 0.00013724 | -1.9547e-07 | 0.00013724 | 0.0027223 | 0.00013724 | 1.3949e-06 | 0.10798 | 2.9604e-08 | 0.10798 | -1.5213e-11 | 0.10798 | 0.00017735 | 0.10064 | 2.7146e-08 | 0.10064 | -1.4527e-11 | 0.10064 | 0.00019198
0.00016038 | -1.9493e-07 | 0.00016038 | -1.9493e-07 | 0.00016038 | 1.4668e-06 | 0.00016113 | -1.9492e-07 | 0.00016113 | 0.00289 | 0.00016113 | 1.4691e-06 | 0.11761 | 3.481e-08 | 0.11761 | -1.6529e-11 | 0.11761 | 0.00017907 | 0.11032 | 3.2334e-08 | 0.11032 | -1.567e-11 | 0.11032 | 0.0001945
0.00018406 | -1.9439e-07 | 0.00018406 | -1.9439e-07 | 0.00018406 | 1.5403e-06 | 0.00018502 | -1.9436e-07 | 0.00018502 | 0.0030357 | 0.00018502 | 1.5433e-06 | 0.12723 | 4.0385e-08 | 0.12723 | -1.8082e-11 | 0.12723 | 0.00018049 | 0.11999 | 3.7922e-08 | 0.11999 | -1.7126e-11 | 0.11999 | 0.0001966
0.0002125 | -1.9373e-07 | 0.0002125 | -1.9373e-07 | 0.0002125 | 1.6286e-06 | 0.00021358 | -1.937e-07 | 0.00021358 | 0.0031868 | 0.00021358 | 1.6319e-06 | 0.13142 | 4.2926e-08 | 0.13142 | -1.8797e-11 | 0.13142 | 0.00018102 | 0.12638 | 4.1824e-08 | 0.12638 | -1.8201e-11 | 0.12638 | 0.00019779
0.00024751 | -1.9292e-07 | 0.00024751 | -1.9292e-07 | 0.00024751 | 1.7373e-06 | 0.00024868 | -1.9289e-07 | 0.00024868 | 0.0033455 | 0.00024868 | 1.7409e-06 | 0.13151 | 4.2979e-08 | 0.13151 | -1.8812e-11 | 0.13151 | 0.00018103 | 0.12763 | 4.2611e-08 | 0.12763 | -1.8417e-11 | 0.12763 | 0.00019801
0.00028781 | -1.9199e-07 | 0.00028781 | -1.9199e-07 | 0.00028781 | 1.8624e-06 | 0.00028378 | -1.9208e-07 | 0.00028378 | 0.0034802 | 0.00028378 | 1.8499e-06 | 0.1316 | 4.3033e-08 | 0.1316 | -1.8825e-11 | 0.1316 | 0.00018104 | 0.12772 | 4.2668e-08 | 0.12772 | -1.8432e-11 | 0.12772 | 0.00019802
0.00032812 | -1.9106e-07 | 0.00032812 | -1.9106e-07 | 0.00032812 | 1.9875e-06 | 0.00032676 | -1.9109e-07 | 0.00032676 | 0.0036196 | 0.00032676 | 1.9833e-06 | 0.13171 | 4.3101e-08 | 0.13171 | -1.8839e-11 | 0.13171 | 0.00018106 | 0.12781 | 4.2724e-08 | 0.12781 | -1.8446e-11 | 0.12781 | 0.00019804
0.00037713 | -1.8992e-07 | 0.00037713 | -1.8992e-07 | 0.00037713 | 2.1397e-06 | 0.00037924 | -1.8988e-07 | 0.00037924 | 0.0037598 | 0.00037924 | 2.1462e-06 | 0.13179 | 4.3152e-08 | 0.13179 | -1.8847e-11 | 0.13179 | 0.00018107 | 0.12791 | 4.2788e-08 | 0.12791 | -1.8458e-11 | 0.12791 | 0.00019806
0.00043669 | -1.8855e-07 | 0.00043669 | -1.8855e-07 | 0.00043669 | 2.3245e-06 | 0.00043874 | -1.885e-07 | 0.00043874 | 0.0038878 | 0.00043874 | 2.3309e-06 | 0.13188 | 4.3204e-08 | 0.13188 | -1.8852e-11 | 0.13188 | 0.00018108 | 0.12799 | 4.2838e-08 | 0.12799 | -1.8465e-11 | 0.12799 | 0.00019807
0.00050413 | -1.8699e-07 | 0.00050413 | -1.8699e-07 | 0.00050413 | 2.5339e-06 | 0.00050465 | -1.8698e-07 | 0.00050465 | 0.0040004 | 0.00050465 | 2.5355e-06 | 0.13198 | 4.3267e-08 | 0.13198 | -1.8855e-11 | 0.13198 | 0.00018109 | 0.12807 | 4.2889e-08 | 0.12807 | -1.847e-11 | 0.12807 | 0.00019808
0.00057876 | -1.8527e-07 | 0.00057876 | -1.8527e-07 | 0.00057876 | 2.7655e-06 | 0.00057878 | -1.8527e-07 | 0.00057878 | 0.0040993 | 0.00057878 | 2.7656e-06 | 0.13209 | 4.3337e-08 | 0.13209 | -1.8855e-11 | 0.13209 | 0.0001811 | 0.12817 | 4.2949e-08 | 0.12817 | -1.8472e-11 | 0.12817 | 0.0001981
0.00066247 | -1.8334e-07 | 0.00066247 | -1.8334e-07 | 0.00066247 | 3.0253e-06 | 0.00066301 | -1.8333e-07 | 0.00066301 | 0.0041853 | 0.00066301 | 3.027e-06 | 0.13221 | 4.3411e-08 | 0.13221 | -1.8854e-11 | 0.13221 | 0.00018112 | 0.12827 | 4.3015e-08 | 0.12827 | -1.8472e-11 | 0.12827 | 0.00019812
0.00075734 | -1.8115e-07 | 0.00075734 | -1.8115e-07 | 0.00075734 | 3.3198e-06 | 0.00075843 | -1.8113e-07 | 0.00075843 | 0.004258 | 0.00075843 | 3.3232e-06 | 0.13238 | 4.3512e-08 | 0.13238 | -1.885e-11 | 0.13238 | 0.00018114 | 0.12839 | 4.3087e-08 | 0.12839 | -1.8471e-11 | 0.12839 | 0.00019814
0.00086487 | -1.7868e-07 | 0.00086487 | -1.7868e-07 | 0.00086487 | 3.6535e-06 | 0.00086612 | -1.7865e-07 | 0.00086612 | 0.0043176 | 0.00086612 | 3.6574e-06 | 0.13262 | 4.3663e-08 | 0.13262 | -1.8843e-11 | 0.13262 | 0.00018117 | 0.12855 | 4.3189e-08 | 0.12855 | -1.8467e-11 | 0.12855 | 0.00019816
0.00098657 | -1.7588e-07 | 0.00098657 | -1.7588e-07 | 0.00098657 | 4.0311e-06 | 0.0009738 | -1.7617e-07 | 0.0009738 | 0.0043604 | 0.0009738 | 3.9915e-06 | 0.13291 | 4.3841e-08 | 0.13291 | -1.8833e-11 | 0.13291 | 0.0001812 | 0.12878 | 4.3339e-08 | 0.12878 | -1.846e-11 | 0.12878 | 0.0001982
0.0011248 | -1.7271e-07 | 0.0011248 | -1.7271e-07 | 0.0011248 | 4.46e-06 | 0.0011065 | -1.7313e-07 | 0.0011065 | 0.0043981 | 0.0011065 | 4.4031e-06 | 0.13323 | 4.4044e-08 | 0.13323 | -1.8821e-11 | 0.13323 | 0.00018124 | 0.12906 | 4.3512e-08 | 0.12906 | -1.845e-11 | 0.12906 | 0.00019825
0.0012831 | -1.6908e-07 | 0.0012831 | -1.6908e-07 | 0.0012831 | 4.9511e-06 | 0.0012666 | -1.6946e-07 | 0.0012666 | 0.0044294 | 0.0012666 | 4.8999e-06 | 0.13367 | 4.4314e-08 | 0.13367 | -1.8804e-11 | 0.13367 | 0.00018129 | 0.12937 | 4.371e-08 | 0.12937 | -1.8438e-11 | 0.12937 | 0.0001983
0.0014668 | -1.6488e-07 | 0.0014668 | -1.6488e-07 | 0.0014668 | 5.5211e-06 | 0.001452 | -1.6522e-07 | 0.001452 | 0.0044541 | 0.001452 | 5.4751e-06 | 0.13431 | 4.4714e-08 | 0.13431 | -1.8779e-11 | 0.13431 | 0.00018137 | 0.12979 | 4.3977e-08 | 0.12979 | -1.8421e-11 | 0.12979 | 0.00019837
0.0016833 | -1.5994e-07 | 0.0016833 | -1.5994e-07 | 0.0016833 | 6.1927e-06 | 0.001666 | -1.6034e-07 | 0.001666 | 0.0044744 | 0.001666 | 6.1391e-06 | 0.13532 | 4.5346e-08 | 0.13532 | -1.874e-11 | 0.13532 | 0.00018148 | 0.13041 | 4.4374e-08 | 0.13041 | -1.8395e-11 | 0.13041 | 0.00019847
0.0019434 | -1.5404e-07 | 0.0019434 | -1.5404e-07 | 0.0019434 | 6.9995e-06 | 0.00188 | -1.5547e-07 | 0.00188 | 0.0044903 | 0.00188 | 6.803e-06 | 0.13704 | 4.6433e-08 | 0.13704 | -1.8673e-11 | 0.13704 | 0.00018167 | 0.13138 | 4.4994e-08 | 0.13138 | -1.8356e-11 | 0.13138 | 0.00019863
0.0022656 | -1.4677e-07 | 0.0022656 | -1.4677e-07 | 0.0022656 | 7.999e-06 | 0.0021748 | -1.4881e-07 | 0.0021748 | 0.0045097 | 0.0021748 | 7.7174e-06 | 0.14041 | 4.8597e-08 | 0.14041 | -1.8543e-11 | 0.14041 | 0.00018202 | 0.133 | 4.6043e-08 | 0.133 | -1.829e-11 | 0.133 | 0.00019888
0.0026774 | -1.3756e-07 | 0.0026774 | -1.3756e-07 | 0.0026774 | 9.2761e-06 | 0.0025809 | -1.3971e-07 | 0.0025809 | 0.0045349 | 0.0025809 | 8.977e-06 | 0.14826 | 5.3797e-08 | 0.14826 | -1.8242e-11 | 0.14826 | 0.00018275 | 0.13611 | 4.8089e-08 | 0.13611 | -1.8163e-11 | 0.13611 | 0.00019935
0.0032254 | -1.2546e-07 | 0.0032254 | -1.2546e-07 | 0.0032254 | 1.0976e-05 | 0.0031206 | -1.2776e-07 | 0.0031206 | 0.0045673 | 0.0031206 | 1.0651e-05 | 0.16632 | 6.66e-08 | 0.16632 | -1.7557e-11 | 0.16632 | 0.00018404 | 0.14331 | 5.2966e-08 | 0.14331 | -1.7871e-11 | 0.14331 | 0.00020034
0.0039924 | -1.0891e-07 | 0.0039924 | -1.0891e-07 | 0.0039924 | 1.3355e-05 | 0.0038416 | -1.1213e-07 | 0.0038416 | 0.0046087 | 0.0038416 | 1.2887e-05 | 0.19265 | 8.7311e-08 | 0.19265 | -1.6567e-11 | 0.19265 | 0.00018521 | 0.16032 | 6.5282e-08 | 0.16032 | -1.7183e-11 | 0.16032 | 0.00020221
0.0050018 | -8.7951e-08 | 0.0050018 | -8.7951e-08 | 0.0050018 | 1.6488e-05 | 0.0048081 | -9.1895e-08 | 0.0048081 | 0.0046581 | 0.0048081 | 1.5887e-05 | 0.21927 | 1.1058e-07 | 0.21927 | -1.5482e-11 | 0.21927 | 0.00018581 | 0.18606 | 8.5963e-08 | 0.18606 | -1.6136e-11 | 0.18606 | 0.00020413
0.006174 | -6.4995e-08 | 0.006174 | -6.4995e-08 | 0.006174 | 2.0129e-05 | 0.0059562 | -6.9138e-08 | 0.0059562 | 0.0047056 | 0.0059562 | 1.9452e-05 | 0.24593 | 1.3612e-07 | 0.24593 | -1.4222e-11 | 0.24593 | 0.00018605 | 0.21206 | 1.0926e-07 | 0.21206 | -1.4981e-11 | 0.21206 | 0.00020527
0.0071442 | -4.7294e-08 | 0.0071442 | -4.7294e-08 | 0.0071442 | 2.3146e-05 | 0.0071042 | -4.8011e-08 | 0.0071042 | 0.0047407 | 0.0071042 | 2.3021e-05 | 0.26286 | 1.5346e-07 | 0.26286 | -1.3135e-11 | 0.26286 | 0.00018608 | 0.22194 | 1.1873e-07 | 0.22194 | -1.4497e-11 | 0.22194 | 0.00020553
0.0081144 | -3.0944e-08 | 0.0081144 | -3.0944e-08 | 0.0081144 | 2.6166e-05 | 0.0082522 | -2.8762e-08 | 0.0082522 | 0.0047649 | 0.0082522 | 2.6596e-05 | 0.27617 | 1.6767e-07 | 0.27617 | -1.1205e-11 | 0.27617 | 0.00018606 | 0.23183 | 1.2854e-07 | 0.23183 | -1.3971e-11 | 0.23183 | 0.00020574
0.0090846 | -1.6083e-08 | 0.0090846 | -1.6083e-08 | 0.0090846 | 2.9192e-05 | 0.0094002 | -1.162e-08 | 0.0094002 | 0.0047808 | 0.0094002 | 3.0177e-05 | 0.28947 | 1.824e-07 | 0.28947 | -8.0448e-12 | 0.28947 | 0.00018601 | 0.24172 | 1.3866e-07 | 0.24172 | -1.3376e-11 | 0.24172 | 0.0002059
0.010105 | -2.2094e-09 | 0.010105 | -2.2094e-09 | 0.010105 | 3.238e-05 | 0.010548 | 3.1457e-09 | 0.010548 | 0.0047905 | 0.010548 | 3.3765e-05 | 0.30598 | 2.0136e-07 | 0.30598 | -7.0176e-12 | 0.30598 | 0.00018592 | 0.26816 | 1.673e-07 | 0.26816 | -9.7599e-12 | 0.26816 | 0.00020614
0.011126 | 9.5999e-09 | 0.011126 | 9.5999e-09 | 0.011126 | 3.5575e-05 | 0.011696 | 1.5277e-08 | 0.011696 | 0.004796 | 0.011696 | 3.7362e-05 | 0.32549 | 2.2475e-07 | 0.32549 | -6.4398e-12 | 0.32549 | 0.00018579 | 0.305 | 2.1088e-07 | 0.305 | -5.7123e-12 | 0.305 | 0.00020618
0.012374 | 2.1245e-08 | 0.012374 | 2.1245e-08 | 0.012374 | 3.9487e-05 | 0.012979 | 2.5783e-08 | 0.012979 | 0.0047989 | 0.012979 | 4.139e-05 | 0.35711 | 2.6485e-07 | 0.35711 | -6.1901e-12 | 0.35711 | 0.00018556 | 0.34184 | 2.5861e-07 | 0.34184 | -4.9918e-12 | 0.34184 | 0.00020602
0.013869 | 3.1165e-08 | 0.013869 | 3.1165e-08 | 0.013869 | 4.4193e-05 | 0.013994 | 3.1792e-08 | 0.013994 | 0.0047994 | 0.013994 | 4.4587e-05 | 0.42328 | 3.5709e-07 | 0.42328 | -7.3115e-12 | 0.42328 | 0.00018506 | 0.37867 | 3.1033e-07 | 0.37867 | -5.0561e-12 | 0.37867 | 0.00020578
0.014376 | 3.352e-08 | 0.014376 | 3.352e-08 | 0.014376 | 4.579e-05 | 0.01444 | 3.3848e-08 | 0.01444 | 0.0047992 | 0.01444 | 4.5993e-05 | 0.48945 | 4.6009e-07 | 0.48945 | -1.0036e-11 | 0.48945 | 0.00018463 | 0.43181 | 3.9162e-07 | 0.43181 | -6.0983e-12 | 0.43181 | 0.00020541
0.014444 | 3.3974e-08 | 0.014444 | 3.3974e-08 | 0.014444 | 4.6003e-05 | 0.01447 | 3.6652e-08 | 0.01447 | 0.0047992 | 0.01447 | 4.5987e-05 | 0.55563 | 5.7313e-07 | 0.55563 | -1.4086e-11 | 0.55563 | 0.00018429 | 0.50156 | 5.0965e-07 | 0.50156 | -8.8341e-12 | 0.50156 | 0.00020499
0.014473 | 3.7243e-08 | 0.014473 | 3.7243e-08 | 0.014473 | 4.5972e-05 | 0.014494 | 4.4159e-08 | 0.014494 | 0.0047992 | 0.014494 | 4.5866e-05 | 0.63004 | 7.1135e-07 | 0.63004 | -2.0023e-11 | 0.63004 | 0.00018403 | 0.57699 | 6.5084e-07 | 0.57699 | -1.3278e-11 | 0.57699 | 0.00020464
0.014501 | 4.7938e-08 | 0.014501 | 4.7938e-08 | 0.014501 | 4.583e-05 | 0.014517 | 5.7842e-08 | 0.014517 | 0.0047992 | 0.014517 | 4.5753e-05 | 0.70445 | 8.605e-07 | 0.70445 | -2.7244e-11 | 0.70445 | 0.00018387 | 0.65588 | 8.1242e-07 | 0.65588 | -1.9358e-11 | 0.65588 | 0.00020439
0.014529 | 6.685e-08 | 0.014529 | 6.685e-08 | 0.014529 | 4.5699e-05 | 0.01455 | 8.3653e-08 | 0.01455 | 0.0047992 | 0.01455 | 4.5643e-05 | 0.79667 | 1.0592e-06 | 0.79667 | -3.7703e-11 | 0.79667 | 0.00018377 | 0.74224 | 1.0043e-06 | 0.74224 | -2.7459e-11 | 0.74224 | 0.00020424
0.014555 | 8.9192e-08 | 0.014555 | 8.9192e-08 | 0.014555 | 4.564e-05 | 0.014574 | 1.0484e-07 | 0.014574 | 0.0047992 | 0.014574 | 4.564e-05 | 0.88889 | 1.272e-06 | 0.88889 | -4.9564e-11 | 0.88889 | 0.00018376 | 0.84003 | 1.2388e-06 | 0.84003 | -3.8158e-11 | 0.84003 | 0.00020417
0.014582 | 1.1215e-07 | 0.014582 | 1.1215e-07 | 0.014582 | 4.5639e-05 | 0.014598 | 1.2469e-07 | 0.014598 | 0.0047991 | 0.014598 | 4.5664e-05 | 1.004 | 1.5551e-06 | 1.004 | -6.5897e-11 | 1.004 | 0.00018383 | 0.95101 | 1.5249e-06 | 0.95101 | -5.188e-11 | 0.95101 | 0.0002042
0.014608 | 1.329e-07 | 0.014608 | 1.329e-07 | 0.014608 | 4.5684e-05 | 0.014624 | 1.4301e-07 | 0.014624 | 0.0047991 | 0.014624 | 4.5722e-05 | 1.1396 | 1.9112e-06 | 1.1396 | -8.679e-11 | 1.1396 | 0.000184 | 1.076 | 1.8698e-06 | 1.076 | -6.8868e-11 | 1.076 | 0.00020432
0.014635 | 1.5018e-07 | 0.014635 | 1.5018e-07 | 0.014635 | 4.5756e-05 | 0.014656 | 1.6069e-07 | 0.014656 | 0.0047991 | 0.014656 | 4.5824e-05 | 1.2911 | 2.3341e-06 | 1.2911 | -1.1158e-10 | 1.2911 | 0.00018425 | 1.2165 | 2.2825e-06 | 1.2165 | -8.935e-11 | 1.2165 | 0.00020453
0.01467 | 1.6656e-07 | 0.01467 | 1.6656e-07 | 0.01467 | 4.5875e-05 | 0.014705 | 1.7805e-07 | 0.014705 | 0.0047991 | 0.014705 | 4.599e-05 | 1.4596 | 2.8306e-06 | 1.4596 | -1.4024e-10 | 1.4596 | 0.00018458 | 1.3751 | 2.7763e-06 | 1.3751 | -1.1363e-10 | 1.3751 | 0.00020482
0.014715 | 1.8101e-07 | 0.014715 | 1.8101e-07 | 0.014715 | 4.6006e-05 | 0.014734 | 1.8591e-07 | 0.014734 | 0.0047991 | 0.014734 | 4.6019e-05 | 1.6505 | 3.4216e-06 | 1.6505 | -1.7339e-10 | 1.6505 | 0.00018496 | 1.5556 | 3.3685e-06 | 1.5556 | -1.4209e-10 | 1.5556 | 0.00020518
0.01475 | 1.8999e-07 | 0.01475 | 1.8999e-07 | 0.01475 | 4.6054e-05 | 0.014764 | 1.9332e-07 | 0.014764 | 0.004799 | 0.014764 | 4.6091e-05 | 1.8712 | 4.1351e-06 | 1.8712 | -2.1191e-10 | 1.8712 | 0.00018539 | 1.7629 | 4.0812e-06 | 1.7629 | -1.7518e-10 | 1.7629 | 0.0002056
0.014785 | 1.9829e-07 | 0.014785 | 1.9829e-07 | 0.014785 | 4.6141e-05 | 0.014847 | 2.11e-07 | 0.014847 | 0.004799 | 0.014847 | 4.6293e-05 | 2.1296 | 5.0036e-06 | 2.1296 | -2.566e-10 | 2.1296 | 0.00018587 | 2.0031 | 4.9426e-06 | 2.0031 | -2.134e-10 | 2.0031 | 0.00020606
0.014893 | 2.1888e-07 | 0.014893 | 2.1888e-07 | 0.014893 | 4.6408e-05 | 0.014999 | 2.3355e-07 | 0.014999 | 0.0047989 | 0.014999 | 4.6694e-05 | 2.4337 | 6.0601e-06 | 2.4337 | -3.08e-10 | 2.4337 | 0.00018637 | 2.2816 | 5.9778e-06 | 2.2816 | -2.5695e-10 | 2.2816 | 0.00020655
0.015037 | 2.3749e-07 | 0.015037 | 2.3749e-07 | 0.015037 | 4.68e-05 | 0.01515 | 2.4702e-07 | 0.01515 | 0.0047987 | 0.01515 | 4.7129e-05 | 2.7637 | 7.2381e-06 | 2.7637 | -3.6196e-10 | 2.7637 | 0.00018682 | 2.5973 | 7.1876e-06 | 2.5973 | -3.0488e-10 | 2.5973 | 0.00020703
0.015181 | 2.4882e-07 | 0.015181 | 2.4882e-07 | 0.015181 | 4.7219e-05 | 0.015263 | 2.5505e-07 | 0.015263 | 0.0047986 | 0.015263 | 4.7441e-05 | 3.1172 | 8.5244e-06 | 3.1172 | -4.1737e-10 | 3.1172 | 0.00018723 | 2.939 | 8.5276e-06 | 2.939 | -3.5471e-10 | 2.939 | 0.00020746
0.015289 | 2.5672e-07 | 0.015289 | 2.5672e-07 | 0.015289 | 4.7507e-05 | 0.015376 | 2.6188e-07 | 0.015376 | 0.0047985 | 0.015376 | 4.7774e-05 | 3.5043 | 9.9527e-06 | 3.5043 | -4.7517e-10 | 3.5043 | 0.00018759 | 3.3094 | 1.0005e-05 | 3.3094 | -4.062e-10 | 3.3094 | 0.00020785
0.015396 | 2.629e-07 | 0.015396 | 2.629e-07 | 0.015396 | 4.7837e-05 | 0.015609 | 2.705e-07 | 0.015609 | 0.0047982 | 0.015609 | 4.8483e-05 | 3.9394 | 1.1573e-05 | 3.9394 | -5.3665e-10 | 3.9394 | 0.00018792 | 3.72 | 1.1661e-05 | 3.72 | -4.6021e-10 | 3.72 | 0.00020819
0.015504 | 2.6718e-07 | 0.015504 | 2.6718e-07 | 0.015504 | 4.8163e-05 | 0.015899 | 2.7484e-07 | 0.015899 | 0.0047979 | 0.015899 | 4.9391e-05 | 4.3745 | 1.3202e-05 | 4.3745 | -5.9457e-10 | 4.3745 | 0.00018817 | 4.1849 | 1.3549e-05 | 4.1849 | -5.1765e-10 | 4.1849 | 0.00020849
0.015787 | 2.736e-07 | 0.015787 | 2.736e-07 | 0.015787 | 4.9038e-05 | 0.016189 | 2.7567e-07 | 0.016189 | 0.0047975 | 0.016189 | 5.031e-05 | 4.9241 | 1.5264e-05 | 4.9241 | -6.6295e-10 | 4.9241 | 0.00018843 | 4.7189 | 1.5727e-05 | 4.7189 | -5.7904e-10 | 4.7189 | 0.00020876
0.016069 | 2.7548e-07 | 0.016069 | 2.7548e-07 | 0.016069 | 4.9929e-05 | 0.01648 | 2.7526e-07 | 0.01648 | 0.004797 | 0.01648 | 5.1233e-05 | 5.6024 | 1.7808e-05 | 5.6024 | -7.405e-10 | 5.6024 | 0.00018867 | 5.3402 | 1.8263e-05 | 5.3402 | -6.4471e-10 | 5.3402 | 0.00020901
0.016352 | 2.7547e-07 | 0.016352 | 2.7547e-07 | 0.016352 | 5.0825e-05 | 0.016786 | 2.7447e-07 | 0.016786 | 0.0047965 | 0.016786 | 5.2208e-05 | 6.4142 | 2.0844e-05 | 6.4142 | -8.2416e-10 | 6.4142 | 0.00018889 | 6.076 | 2.1259e-05 | 6.076 | -7.1512e-10 | 6.076 | 0.00020922
0.016634 | 2.7486e-07 | 0.016634 | 2.7486e-07 | 0.016634 | 5.1724e-05 | 0.017212 | 2.7328e-07 | 0.017212 | 0.0047958 | 0.017212 | 5.3561e-05 | 7.3916 | 2.448e-05 | 7.3916 | -9.1299e-10 | 7.3916 | 0.00018908 | 6.9694 | 2.4883e-05 | 6.9694 | -7.9093e-10 | 6.9694 | 0.00020942
0.016997 | 2.7388e-07 | 0.016997 | 2.7388e-07 | 0.016997 | 5.2876e-05 | 0.017933 | 2.7127e-07 | 0.017933 | 0.0047944 | 0.017933 | 5.5851e-05 | 8.6205 | 2.9017e-05 | 8.6205 | -1.0085e-09 | 8.6205 | 0.00018925 | 8.0924 | 2.9406e-05 | 8.0924 | -8.7289e-10 | 8.0924 | 0.00020959
0.017561 | 2.723e-07 | 0.017561 | 2.723e-07 | 0.017561 | 5.4669e-05 | 0.01923 | 2.6789e-07 | 0.01923 | 0.0047917 | 0.01923 | 5.9965e-05 | 10.2714 | 3.5046e-05 | 10.2714 | -1.1126e-09 | 10.2714 | 0.0001894 | 9.5699 | 3.53e-05 | 9.5699 | -9.6138e-10 | 9.5699 | 0.00020973
0.018524 | 2.6967e-07 | 0.018524 | 2.6967e-07 | 0.018524 | 5.7728e-05 | 0.021444 | 2.6296e-07 | 0.021444 | 0.0047865 | 0.021444 | 6.697e-05 | 12.6763 | 4.3696e-05 | 12.6763 | -1.2247e-09 | 12.6763 | 0.00018951 | 11.6379 | 4.344e-05 | 11.6379 | -1.0552e-09 | 11.6379 | 0.00020985
0.020157 | 2.6569e-07 | 0.020157 | 2.6569e-07 | 0.020157 | 6.2902e-05 | 0.023039 | 2.6028e-07 | 0.023039 | 0.0047825 | 0.023039 | 7.2004e-05 | 14.0598 | 4.86e-05 | 14.0598 | -1.2706e-09 | 14.0598 | 0.00018953 | 12.8435 | 4.8126e-05 | 12.8435 | -1.0957e-09 | 12.8435 | 0.00020987
0.02247 | 2.6108e-07 | 0.02247 | 2.6108e-07 | 0.02247 | 7.0209e-05 | 0.023734 | 2.5928e-07 | 0.023734 | 0.0047807 | 0.023734 | 7.4193e-05 | 14.6125 | 5.0545e-05 | 14.6125 | -1.2858e-09 | 14.6125 | 0.00018954 | 14.6158 | 5.4936e-05 | 14.6158 | -1.1411e-09 | 14.6158 | 0.00020989
0.023477 | 2.5965e-07 | 0.023477 | 2.5965e-07 | 0.023477 | 7.3384e-05 | 0.023957 | 2.5896e-07 | 0.023957 | 0.0047801 | 0.023957 | 7.4895e-05 | 14.7739 | 5.1111e-05 | 14.7739 | -1.2898e-09 | 14.7739 | 0.00018954 | 14.8126 | 5.5686e-05 | 14.8126 | -1.1453e-09 | 14.8126 | 0.00020989
0.023757 | 2.5925e-07 | 0.023757 | 2.5925e-07 | 0.023757 | 7.4267e-05 | 0.024179 | 2.5864e-07 | 0.024179 | 0.0047795 | 0.024179 | 7.5597e-05 | 14.9353 | 5.1677e-05 | 14.9353 | -1.2936e-09 | 14.9353 | 0.00018954 | 15.0095 | 5.6436e-05 | 15.0095 | -1.1493e-09 | 15.0095 | 0.00020989
0.02392 | 2.5901e-07 | 0.02392 | 2.5901e-07 | 0.02392 | 7.478e-05 | 0.024411 | 2.5832e-07 | 0.024411 | 0.0047789 | 0.024411 | 7.6327e-05 | 15.0968 | 5.2242e-05 | 15.0968 | -1.2975e-09 | 15.0968 | 0.00018954 | 15.2063 | 5.7184e-05 | 15.2063 | -1.1532e-09 | 15.2063 | 0.00020988
0.024083 | 2.5877e-07 | 0.024083 | 2.5877e-07 | 0.024083 | 7.5292e-05 | 0.024644 | 2.58e-07 | 0.024644 | 0.0047783 | 0.024644 | 7.7057e-05 | 15.2582 | 5.2806e-05 | 15.2582 | -1.3013e-09 | 15.2582 | 0.00018954 | 16.3475 | 6.1501e-05 | 16.3475 | -1.1725e-09 | 16.3475 | 0.00020987
0.024279 | 2.5849e-07 | 0.024279 | 2.5849e-07 | 0.024279 | 7.591e-05 | 0.024925 | 2.5764e-07 | 0.024925 | 0.0047775 | 0.024925 | 7.7943e-05 | 15.4801 | 5.3581e-05 | 15.4801 | -1.3064e-09 | 15.4801 | 0.00018954 | 18.6634 | 7.0145e-05 | 18.6634 | -1.1984e-09 | 18.6634 | 0.00020983
0.024475 | 2.5822e-07 | 0.024475 | 2.5822e-07 | 0.024475 | 7.6528e-05 | 0.025318 | 2.5716e-07 | 0.025318 | 0.0047765 | 0.025318 | 7.9178e-05 | 15.73 | 5.4452e-05 | 15.73 | -1.3119e-09 | 15.73 | 0.00018954 | 21.0268 | 7.881e-05 | 21.0268 | -1.2096e-09 | 21.0268 | 0.00020977
0.024767 | 2.5784e-07 | 0.024767 | 2.5784e-07 | 0.024767 | 7.7444e-05 | 0.025959 | 2.5642e-07 | 0.025959 | 0.0047748 | 0.025959 | 8.1193e-05 | 16.0203 | 5.5461e-05 | 16.0203 | -1.318e-09 | 16.0203 | 0.00018954 | 23.3398 | 8.7138e-05 | 23.3398 | -1.2093e-09 | 23.3398 | 0.00020971
0.025058 | 2.5747e-07 | 0.025058 | 2.5747e-07 | 0.025058 | 7.8361e-05 | 0.027004 | 2.553e-07 | 0.027004 | 0.0047721 | 0.027004 | 8.4471e-05 | 16.4051 | 5.6796e-05 | 16.4051 | -1.3255e-09 | 16.4051 | 0.00018954 | 26.1247 | 9.6972e-05 | 26.1247 | -1.1985e-09 | 26.1247 | 0.00020962
0.025503 | 2.5694e-07 | 0.025503 | 2.5694e-07 | 0.025503 | 7.9759e-05 | 0.028713 | 2.5344e-07 | 0.028713 | 0.0047676 | 0.028713 | 8.9827e-05 | 16.9068 | 5.853e-05 | 16.9068 | -1.3344e-09 | 16.9068 | 0.00018953 | 29.3498 | 0.0001081 | 29.3498 | -1.176e-09 | 29.3498 | 0.00020952
0.026279 | 2.5608e-07 | 0.026279 | 2.5608e-07 | 0.026279 | 8.2195e-05 | 0.031739 | 2.5176e-07 | 0.031739 | 0.0047596 | 0.031739 | 9.9281e-05 | 17.6382 | 6.1046e-05 | 17.6382 | -1.3457e-09 | 17.6382 | 0.00018953 | 32.8285 | 0.0001198 | 32.8285 | -1.144e-09 | 32.8285 | 0.00020942
0.027578 | 2.5462e-07 | 0.027578 | 2.5462e-07 | 0.027578 | 8.6273e-05 | 0.035176 | 2.517e-07 | 0.035176 | 0.0047504 | 0.035176 | 0.00010997 | 19.3254 | 6.6797e-05 | 19.3254 | -1.3651e-09 | 19.3254 | 0.0001895 | 36.521 | 0.00013187 | 36.521 | -1.105e-09 | 36.521 | 0.00020931
0.029713 | 2.5269e-07 | 0.029713 | 2.5269e-07 | 0.029713 | 9.2958e-05 | 0.037296 | 2.5518e-07 | 0.037296 | 0.0047448 | 0.037296 | 0.00011653 | 22.24 | 7.6558e-05 | 22.24 | -1.3807e-09 | 22.24 | 0.00018944 | 40.4882 | 0.00014447 | 40.4882 | -1.0603e-09 | 40.4882 | 0.00020921
0.033285 | 2.5146e-07 | 0.033285 | 2.5146e-07 | 0.033285 | 0.0001041 | 0.039415 | 2.6373e-07 | 0.039415 | 0.0047391 | 0.039415 | 0.00012304 | 25.3287 | 8.6667e-05 | 25.3287 | -1.3782e-09 | 25.3287 | 0.00018937 | 44.8083 | 0.00015776 | 44.8083 | -1.011e-09 | 44.8083 | 0.0002091
0.036857 | 2.5231e-07 | 0.036857 | 2.5231e-07 | 0.036857 | 0.00011519 | 0.039701 | 2.6147e-07 | 0.039701 | 0.0047383 | 0.039701 | 0.00012395 | 28.326 | 9.625e-05 | 28.326 | -1.3626e-09 | 28.326 | 0.00018929 | 49.5377 | 0.00017181 | 49.5377 | -9.5821e-10 | 49.5377 | 0.000209
0.036948 | 2.5581e-07 | 0.036948 | 2.5581e-07 | 0.036948 | 0.00011541 | 0.039912 | 2.6093e-07 | 0.039912 | 0.0047377 | 0.039912 | 0.00012459 | 31.6343 | 0.00010657 | 31.6343 | -1.3355e-09 | 31.6343 | 0.00018921 | 54.7148 | 0.00018661 | 54.7148 | -9.0311e-10 | 54.7148 | 0.00020889
0.037017 | 2.5782e-07 | 0.037017 | 2.5782e-07 | 0.037017 | 0.00011565 | 0.040124 | 2.6102e-07 | 0.040124 | 0.0047372 | 0.040124 | 0.00012525 | 35.2806 | 0.00011765 | 35.2806 | -1.2982e-09 | 35.2806 | 0.00018912 | 60.3795 | 0.00020213 | 60.3795 | -8.4691e-10 | 60.3795 | 0.00020878
0.037086 | 2.5884e-07 | 0.037086 | 2.5884e-07 | 0.037086 | 0.00011585 | 0.040392 | 2.6121e-07 | 0.040392 | 0.0047364 | 0.040392 | 0.00012608 | 39.2575 | 0.00012939 | 39.2575 | -1.2526e-09 | 39.2575 | 0.00018904 | 66.5882 | 0.00021838 | 66.5882 | -7.9048e-10 | 66.5882 | 0.00020867
0.037195 | 2.5969e-07 | 0.037195 | 2.5969e-07 | 0.037195 | 0.00011619 | 0.04079 | 2.6142e-07 | 0.04079 | 0.0047354 | 0.04079 | 0.0001273 | 43.5664 | 0.0001417 | 43.5664 | -1.2008e-09 | 43.5664 | 0.00018895 | 73.4129 | 0.00023535 | 73.4129 | -7.344e-10 | 73.4129 | 0.00020856
0.037343 | 2.6012e-07 | 0.037343 | 2.6012e-07 | 0.037343 | 0.00011665 | 0.041523 | 2.6179e-07 | 0.041523 | 0.0047334 | 0.041523 | 0.00012956 | 48.2386 | 0.0001546 | 48.2386 | -1.1446e-09 | 48.2386 | 0.00018886 | 80.8894 | 0.00025294 | 80.8894 | -6.7937e-10 | 80.8894 | 0.00020845
0.037533 | 2.6026e-07 | 0.037533 | 2.6026e-07 | 0.037533 | 0.00011724 | 0.044164 | 2.6336e-07 | 0.044164 | 0.0047262 | 0.044164 | 0.00013769 | 53.3253 | 0.00016812 | 53.3253 | -1.0853e-09 | 53.3253 | 0.00018876 | 89.1926 | 0.00027129 | 89.1926 | -6.2493e-10 | 89.1926 | 0.00020833
0.037783 | 2.6031e-07 | 0.037783 | 2.6031e-07 | 0.037783 | 0.00011801 | 0.048836 | 2.6716e-07 | 0.048836 | 0.0047134 | 0.048836 | 0.00015201 | 58.8849 | 0.00018231 | 58.8849 | -1.0241e-09 | 58.8849 | 0.00018867 | 98.3446 | 0.00029017 | 98.3446 | -5.7155e-10 | 98.3446 | 0.00020822
0.038145 | 2.6039e-07 | 0.038145 | 2.6039e-07 | 0.038145 | 0.00011913 | 0.055716 | 2.7473e-07 | 0.055716 | 0.0046944 | 0.055716 | 0.00017295 | 64.9748 | 0.00019715 | 64.9748 | -9.622e-10 | 64.9748 | 0.00018858 | 108.441 | 0.00030946 | 108.441 | -5.19e-10 | 108.441 | 0.0002081
0.038761 | 2.6057e-07 | 0.038761 | 2.6057e-07 | 0.038761 | 0.00012104 | 0.06331 | 2.8534e-07 | 0.06331 | 0.0046731 | 0.06331 | 0.00019588 | 71.6581 | 0.00021266 | 71.6581 | -9.0039e-10 | 71.6581 | 0.00018849 | 119.6338 | 0.00032909 | 119.6338 | -4.6667e-10 | 119.6338 | 0.00020798
0.04011 | 2.6107e-07 | 0.04011 | 2.6107e-07 | 0.04011 | 0.0001252 | 0.071602 | 2.9834e-07 | 0.071602 | 0.0046495 | 0.071602 | 0.0002207 | 79.0085 | 0.0002288 | 79.0085 | -8.3931e-10 | 79.0085 | 0.0001884 | 132.0942 | 0.00034894 | 132.0942 | -4.1392e-10 | 132.0942 | 0.00020786
0.044515 | 2.6341e-07 | 0.044515 | 2.6341e-07 | 0.044515 | 0.00013877 | 0.071723 | 3.0134e-07 | 0.071723 | 0.0046491 | 0.071723 | 0.00022101 | 87.1004 | 0.00024553 | 87.1004 | -7.7938e-10 | 87.1004 | 0.0001883 | 145.9716 | 0.00036879 | 145.9716 | -3.602e-10 | 145.9716 | 0.00020773
0.051035 | 2.692e-07 | 0.051035 | 2.692e-07 | 0.051035 | 0.00015872 | 0.071812 | 3.0267e-07 | 0.071812 | 0.0046489 | 0.071812 | 0.0002213 | 96.0353 | 0.0002628 | 96.0353 | -7.2062e-10 | 96.0353 | 0.00018821 | 161.5376 | 0.00038849 | 161.5376 | -3.0465e-10 | 161.5376 | 0.0002076
0.057554 | 2.7737e-07 | 0.057554 | 2.7737e-07 | 0.057554 | 0.00017852 | 0.071902 | 3.0318e-07 | 0.071902 | 0.0046486 | 0.071902 | 0.00022156 | 105.9342 | 0.00028055 | 105.9342 | -6.628e-10 | 105.9342 | 0.00018811 | 179.0013 | 0.00040769 | 179.0013 | -2.4679e-10 | 179.0013 | 0.00020747
0.064441 | 2.8714e-07 | 0.064441 | 2.8714e-07 | 0.064441 | 0.00019928 | 0.072022 | 3.0353e-07 | 0.072022 | 0.0046483 | 0.072022 | 0.00022192 | 116.8488 | 0.00029856 | 116.8488 | -6.0593e-10 | 116.8488 | 0.00018802 | 198.5816 | 0.00042601 | 198.5816 | -1.8626e-10 | 198.5816 | 0.00020733
0.072623 | 3.0086e-07 | 0.072623 | 3.0086e-07 | 0.072623 | 0.00022373 | 0.072188 | 3.0383e-07 | 0.072188 | 0.0046478 | 0.072188 | 0.00022242 | 128.9392 | 0.00031675 | 128.9392 | -5.4932e-10 | 128.9392 | 0.00018792 | 220.6107 | 0.00044311 | 220.6107 | -1.2253e-10 | 220.6107 | 0.00020719
0.083122 | 3.2359e-07 | 0.083122 | 3.2359e-07 | 0.083122 | 0.00025477 | 0.072432 | 3.042e-07 | 0.072432 | 0.0046471 | 0.072432 | 0.00022314 | 142.3925 | 0.00033498 | 142.3925 | -4.9223e-10 | 142.3925 | 0.00018782 | 244.6576 | 0.00045814 | 244.6576 | -5.7229e-11 | 244.6576 | 0.00020705
0.084311 | 3.2342e-07 | 0.084311 | 3.2342e-07 | 0.084311 | 0.00025828 | 0.072813 | 3.0479e-07 | 0.072813 | 0.004646 | 0.072813 | 0.00022428 | 157.408 | 0.00035306 | 157.408 | -4.3398e-10 | 157.408 | 0.00018772 | 282.3229 | 0.00047558 | 282.3229 | 3.8079e-11 | 282.3229 | 0.00020684
0.084966 | 3.2481e-07 | 0.084966 | 3.2481e-07 | 0.084966 | 0.0002602 | 0.073489 | 3.0586e-07 | 0.073489 | 0.004644 | 0.073489 | 0.00022629 | 174.1665 | 0.00037071 | 174.1665 | -3.7414e-10 | 174.1665 | 0.00018762 | 326.5765 | 0.00048852 | 326.5765 | 1.4136e-10 | 326.5765 | 0.00020662
0.085621 | 3.2601e-07 | 0.085621 | 3.2601e-07 | 0.085621 | 0.00026213 | 0.074959 | 3.082e-07 | 0.074959 | 0.0046398 | 0.074959 | 0.00023065 | 193.0618 | 0.00038779 | 193.0618 | -3.1168e-10 | 193.0618 | 0.00018751 | 372.9453 | 0.00049555 | 372.9453 | 2.4184e-10 | 372.9453 | 0.00020641
0.086276 | 3.2711e-07 | 0.086276 | 3.2711e-07 | 0.086276 | 0.00026405 | 0.078823 | 3.1444e-07 | 0.078823 | 0.0046286 | 0.078823 | 0.0002421 | 212.7842 | 0.00040279 | 212.7842 | -2.5101e-10 | 212.7842 | 0.00018741 | 448.5288 | 0.00049803 | 448.5288 | 3.9402e-10 | 448.5288 | 0.00020611
0.087831 | 3.2976e-07 | 0.087831 | 3.2976e-07 | 0.087831 | 0.0002686 | 0.087632 | 3.2906e-07 | 0.087632 | 0.0046027 | 0.087632 | 0.00026802 | 245.4066 | 0.00042242 | 245.4066 | -1.5842e-10 | 245.4066 | 0.00018726 | 514.7256 | 0.00049381 | 514.7256 | 5.1808e-10 | 514.7256 | 0.00020588
0.090369 | 3.3413e-07 | 0.090369 | 3.3413e-07 | 0.090369 | 0.00027602 | 0.10501 | 3.5892e-07 | 0.10501 | 0.0045503 | 0.10501 | 0.00031843 | 287.2114 | 0.00043989 | 287.2114 | -5.0998e-11 | 287.2114 | 0.00018709 | 618.993 | 0.00048172 | 618.993 | 7.0273e-10 | 618.993 | 0.00020555
0.095299 | 3.4267e-07 | 0.095299 | 3.4267e-07 | 0.095299 | 0.00029037 | 0.12473 | 3.9404e-07 | 0.12473 | 0.0044889 | 0.12473 | 0.00037446 | 330.6263 | 0.00045099 | 330.6263 | 5.0211e-11 | 330.6263 | 0.00018693 | 621.4008 | 0.00048136 | 621.4008 | 7.0684e-10 | 621.4008 | 0.00020554
0.10958 | 3.6741e-07 | 0.10958 | 3.6741e-07 | 0.10958 | 0.00033153 | 0.14444 | 4.2862e-07 | 0.14444 | 0.0044252 | 0.14444 | 0.00042928 | 375.38 | 0.00045696 | 375.38 | 1.4624e-10 | 375.38 | 0.00018679 | 622.4111 | 0.00048122 | 622.4111 | 7.0857e-10 | 622.4111 | 0.00020554
0.13154 | 4.0566e-07 | 0.13154 | 4.0566e-07 | 0.13154 | 0.00039355 | 0.16416 | 4.6246e-07 | 0.16416 | 0.0043593 | 0.16416 | 0.00048291 | 424.9566 | 0.00045904 | 424.9566 | 2.4524e-10 | 424.9566 | 0.00018665 | 622.5602 | 0.00048119 | 622.5602 | 7.0882e-10 | 622.5602 | 0.00020554
0.1535 | 4.4466e-07 | 0.1535 | 4.4466e-07 | 0.1535 | 0.00045408 | 0.18038 | 4.871e-07 | 0.18038 | 0.0043035 | 0.18038 | 0.00052617 | 513.994 | 0.00045572 | 513.994 | 4.0985e-10 | 513.994 | 0.00018643 | 622.5907 | 0.00048119 | 622.5907 | 7.0887e-10 | 622.5907 | 0.00020553
0.16911 | 4.7008e-07 | 0.16911 | 4.7008e-07 | 0.16911 | 0.00049621 | 0.1966 | 5.1188e-07 | 0.1966 | 0.0042461 | 0.1966 | 0.00056863 | 596.7444 | 0.00044731 | 596.7444 | 5.511e-10 | 596.7444 | 0.00018626 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.18472 | 4.9398e-07 | 0.18472 | 4.9398e-07 | 0.18472 | 0.00053761 | 0.21282 | 5.3568e-07 | 0.21282 | 0.0041872 | 0.21282 | 0.00061032 | 684.1911 | 0.00043598 | 684.1911 | 6.9221e-10 | 684.1911 | 0.0001861 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.20727 | 5.2769e-07 | 0.20727 | 5.2769e-07 | 0.20727 | 0.00059615 | 0.23134 | 5.6189e-07 | 0.23134 | 0.0041183 | 0.23134 | 0.00065695 | 688.1714 | 0.00043542 | 688.1714 | 6.9846e-10 | 688.1714 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.23499 | 5.6711e-07 | 0.23499 | 5.6711e-07 | 0.23499 | 0.00066603 | 0.26032 | 6.0123e-07 | 0.26032 | 0.0040065 | 0.26032 | 0.00072798 | 688.9214 | 0.00043531 | 688.9214 | 6.9963e-10 | 688.9214 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.26456 | 6.0711e-07 | 0.26456 | 6.0711e-07 | 0.26456 | 0.00073816 | 0.29425 | 6.4519e-07 | 0.29425 | 0.0038699 | 0.29425 | 0.0008081 | 689.1669 | 0.00043528 | 689.1669 | 7.0002e-10 | 689.1669 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.29525 | 6.468e-07 | 0.29525 | 6.468e-07 | 0.29525 | 0.0008104 | 0.32909 | 6.8854e-07 | 0.32909 | 0.0037237 | 0.32909 | 0.00088705 | 689.294 | 0.00043526 | 689.294 | 7.0022e-10 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.32594 | 6.8512e-07 | 0.32594 | 6.8512e-07 | 0.32594 | 0.00088003 | 0.36393 | 7.3063e-07 | 0.36393 | 0.0035719 | 0.36393 | 0.00096273 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.35982 | 7.263e-07 | 0.35982 | 7.263e-07 | 0.35982 | 0.00095396 | 0.39877 | 7.7191e-07 | 0.39877 | 0.0034151 | 0.39877 | 0.0010352 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.39529 | 7.6854e-07 | 0.39529 | 7.6854e-07 | 0.39529 | 0.0010281 | 0.43508 | 8.1492e-07 | 0.43508 | 0.0032469 | 0.43508 | 0.0011075 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.43076 | 8.1065e-07 | 0.43076 | 8.1065e-07 | 0.43076 | 0.0010991 | 0.4749 | 8.6136e-07 | 0.4749 | 0.0030582 | 0.4749 | 0.0011831 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.46995 | 8.5676e-07 | 0.46995 | 8.5676e-07 | 0.46995 | 0.0011739 | 0.5205 | 9.1374e-07 | 0.5205 | 0.0028381 | 0.5205 | 0.001265 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.5148 | 9.0851e-07 | 0.5148 | 9.0851e-07 | 0.5148 | 0.001255 | 0.57447 | 9.7563e-07 | 0.57447 | 0.002575 | 0.57447 | 0.0013559 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.56827 | 9.7022e-07 | 0.56827 | 9.7022e-07 | 0.56827 | 0.0013458 | 0.62902 | 1.0378e-06 | 0.62902 | 0.0023106 | 0.62902 | 0.0014415 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.62175 | 1.0316e-06 | 0.62175 | 1.0316e-06 | 0.62175 | 0.0014304 | 0.68987 | 1.1066e-06 | 0.68987 | 0.0020237 | 0.68987 | 0.0015298 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3569e-08 | 622.5907 | 0.00020553
0.68224 | 1.1005e-06 | 0.68224 | 1.1005e-06 | 0.68224 | 0.0015191 | 0.73719 | 1.1595e-06 | 0.73719 | 0.001812 | 0.73719 | 0.0015936 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.357e-08 | 622.5907 | 0.00020553
0.73043 | 1.155e-06 | 0.73043 | 1.155e-06 | 0.73043 | 0.0015848 | 0.78451 | 1.2106e-06 | 0.78451 | 0.0016152 | 0.78451 | 0.0016535 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.357e-08 | 622.5907 | 0.00020553
0.77863 | 1.2077e-06 | 0.77863 | 1.2077e-06 | 0.77863 | 0.0016462 | 0.82298 | 1.2517e-06 | 0.82298 | 0.0014701 | 0.82298 | 0.0016993 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3571e-08 | 622.5907 | 0.00020553
0.81751 | 1.2497e-06 | 0.81751 | 1.2497e-06 | 0.81751 | 0.0016929 | 0.86145 | 1.2917e-06 | 0.86145 | 0.0013411 | 0.86145 | 0.0017427 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3574e-08 | 622.5907 | 0.00020553
0.85639 | 1.2906e-06 | 0.85639 | 1.2906e-06 | 0.85639 | 0.0017371 | 0.90075 | 1.3316e-06 | 0.90075 | 0.0012281 | 0.90075 | 0.0017847 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3579e-08 | 622.5907 | 0.00020553
0.89527 | 1.3306e-06 | 0.89527 | 1.3306e-06 | 0.89527 | 0.0017789 | 0.94005 | 1.3704e-06 | 0.94005 | 0.0011359 | 0.94005 | 0.0018244 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3587e-08 | 622.5907 | 0.00020553
0.93415 | 1.3696e-06 | 0.93415 | 1.3696e-06 | 0.93415 | 0.0018185 | 0.94497 | 1.3752e-06 | 0.94497 | 0.0011262 | 0.94497 | 0.0018292 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.3605e-08 | 622.5907 | 0.00020553
0.94532 | 1.3806e-06 | 0.94532 | 1.3806e-06 | 0.94532 | 0.0018295 | 0.94722 | 1.3774e-06 | 0.94722 | 0.0011218 | 0.94722 | 0.0018314 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5907 | 0.00048119 | 622.5907 | 2.363e-08 | 622.5907 | 0.00020553
0.94708 | 1.3823e-06 | 0.94708 | 1.3823e-06 | 0.94708 | 0.0018312 | 0.94782 | 1.3779e-06 | 0.94782 | 0.0011205 | 0.94782 | 0.0018319 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5908 | 0.00048119 | 622.5908 | 2.3657e-08 | 622.5908 | 0.00020553
0.94779 | 1.383e-06 | 0.94779 | 1.383e-06 | 0.94779 | 0.0018319 | 0.94843 | 1.3785e-06 | 0.94843 | 0.001119 | 0.94843 | 0.0018325 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5908 | 0.00048119 | 622.5908 | 2.3689e-08 | 622.5908 | 0.00020553
0.94849 | 1.3837e-06 | 0.94849 | 1.3837e-06 | 0.94849 | 0.0018326 | 0.9492 | 1.3793e-06 | 0.9492 | 0.0011169 | 0.9492 | 0.0018333 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5908 | 0.00048119 | 622.5908 | 2.3736e-08 | 622.5908 | 0.00020553
0.94925 | 1.3845e-06 | 0.94925 | 1.3845e-06 | 0.94925 | 0.0018333 | 0.94997 | 1.38e-06 | 0.94997 | 0.0011145 | 0.94997 | 0.001834 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5909 | 0.00048119 | 622.5909 | 2.3833e-08 | 622.5909 | 0.00020553
0.95002 | 1.3852e-06 | 0.95002 | 1.3852e-06 | 0.95002 | 0.0018341 | 0.95074 | 1.3808e-06 | 0.95074 | 0.0011119 | 0.95074 | 0.0018348 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5912 | 0.00048119 | 622.5912 | 2.4206e-08 | 622.5912 | 0.00020553
0.95078 | 1.386e-06 | 0.95078 | 1.386e-06 | 0.95078 | 0.0018348 | 0.95202 | 1.382e-06 | 0.95202 | 0.0011076 | 0.95202 | 0.001836 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5916 | 0.00048119 | 622.5916 | 2.4856e-08 | 622.5916 | 0.00020553
0.95201 | 1.3872e-06 | 0.95201 | 1.3872e-06 | 0.95201 | 0.001836 | 0.95329 | 1.3832e-06 | 0.95329 | 0.0011032 | 0.95329 | 0.0018372 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5923 | 0.00048119 | 622.5923 | 2.6038e-08 | 622.5923 | 0.00020553
0.95324 | 1.3884e-06 | 0.95324 | 1.3884e-06 | 0.95324 | 0.0018372 | 0.95457 | 1.3845e-06 | 0.95457 | 0.0010989 | 0.95457 | 0.0018385 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5937 | 0.00048119 | 622.5937 | 2.8971e-08 | 622.5937 | 0.00020553
0.95446 | 1.3896e-06 | 0.95446 | 1.3896e-06 | 0.95446 | 0.0018383 | 0.95584 | 1.3857e-06 | 0.95584 | 0.0010946 | 0.95584 | 0.0018397 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.5971 | 0.00048119 | 622.5971 | 3.8417e-08 | 622.5971 | 0.00020553
0.95588 | 1.3909e-06 | 0.95588 | 1.3909e-06 | 0.95588 | 0.0018397 | 0.95802 | 1.3878e-06 | 0.95802 | 0.0010873 | 0.95802 | 0.0018418 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.6018 | 0.00048119 | 622.6018 | 5.7285e-08 | 622.6018 | 0.00020553
0.95821 | 1.3932e-06 | 0.95821 | 1.3932e-06 | 0.95821 | 0.0018419 | 0.96673 | 1.3962e-06 | 0.96673 | 0.0010597 | 0.96673 | 0.00185 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.6091 | 0.00048119 | 622.6091 | 9.8645e-08 | 622.6091 | 0.00020553
0.96647 | 1.4012e-06 | 0.96647 | 1.4012e-06 | 0.96647 | 0.0018498 | 0.97726 | 1.4062e-06 | 0.97726 | 0.001029 | 0.97726 | 0.0018599 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.6164 | 0.00048119 | 622.6164 | 1.5405e-07 | 622.6164 | 0.00020553
0.97904 | 1.4134e-06 | 0.97904 | 1.4134e-06 | 0.97904 | 0.0018615 | 0.98736 | 1.4158e-06 | 0.98736 | 0.0010029 | 0.98736 | 0.0018692 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.6237 | 0.00048119 | 622.6237 | 2.226e-07 | 622.6237 | 0.00020553
0.98861 | 1.4225e-06 | 0.98861 | 1.4225e-06 | 0.98861 | 0.0018704 | 0.99039 | 1.4186e-06 | 0.99039 | 0.0009971 | 0.99039 | 0.001872 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.6311 | 0.00048118 | 622.6311 | 3.0479e-07 | 622.6311 | 0.00020553
0.99147 | 1.4252e-06 | 0.99147 | 1.4252e-06 | 0.99147 | 0.001873 | 0.99342 | 1.4215e-06 | 0.99342 | 0.00099221 | 0.99342 | 0.0018748 | 689.294 | 0.00043526 | 689.294 | 1.2433e-06 | 689.294 | 0.00018609 | 622.6405 | 0.00048118 | 622.6405 | 4.2596e-07 | 622.6405 | 0.00020553
0.99433 | 1.4279e-06 | 0.99433 | 1.4279e-06 | 0.99433 | 0.0018756 | 0.99646 | 1.4243e-06 | 0.99646 | 0.00098783 | 0.99646 | 0.0018775 | 689.2941 | 0.00043526 | 689.2941 | 1.2433e-06 | 689.2941 | 0.00018609 | 622.6513 | 0.00048118 | 622.6513 | 5.8609e-07 | 622.6513 | 0.00020553
0.99719 | 1.4306e-06 | 0.99719 | 1.4306e-06 | 0.99719 | 0.0018782 | 1.0005 | 1.4281e-06 | 1.0005 | 0.00098244 | 1.0005 | 0.0018812 | 689.2941 | 0.00043526 | 689.2941 | 1.2434e-06 | 689.2941 | 0.00018609 | 622.6636 | 0.00048118 | 622.6636 | 7.9102e-07 | 622.6636 | 0.00020553
1.0016 | 1.4348e-06 | 1.0016 | 1.4348e-06 | 1.0016 | 0.0018821 | 1.0063 | 1.4334e-06 | 1.0063 | 0.00097541 | 1.0063 | 0.0018863 | 689.2941 | 0.00043526 | 689.2941 | 1.2434e-06 | 689.2941 | 0.00018609 | 622.6759 | 0.00048118 | 622.6759 | 1.0177e-06 | 622.6759 | 0.00020553
1.0079 | 1.4407e-06 | 1.0079 | 1.4407e-06 | 1.0079 | 0.0018878 | 1.0132 | 1.4399e-06 | 1.0132 | 0.00096725 | 1.0132 | 0.0018925 | 689.2941 | 0.00043526 | 689.2941 | 1.2434e-06 | 689.2941 | 0.00018609 | 622.6912 | 0.00048118 | 622.6912 | 1.3257e-06 | 622.6912 | 0.00020553
1.0142 | 1.4466e-06 | 1.0142 | 1.4466e-06 | 1.0142 | 0.0018933 | 1.021 | 1.447e-06 | 1.021 | 0.00095795 | 1.021 | 0.0018994 | 689.2941 | 0.00043526 | 689.2941 | 1.2435e-06 | 689.2941 | 0.00018609 | 622.7131 | 0.00048117 | 622.7131 | 1.805e-06 | 622.7131 | 0.00020553
1.0217 | 1.4535e-06 | 1.0217 | 1.4535e-06 | 1.0217 | 0.0018999 | 1.0298 | 1.4551e-06 | 1.0298 | 0.00094666 | 1.0298 | 0.001907 | 689.2941 | 0.00043526 | 689.2941 | 1.2435e-06 | 689.2941 | 0.00018609 | 622.7428 | 0.00048117 | 622.7428 | 2.5041e-06 | 622.7428 | 0.00020553
1.0309 | 1.4621e-06 | 1.0309 | 1.4621e-06 | 1.0309 | 0.0019079 | 1.0391 | 1.4635e-06 | 1.0391 | 0.00093266 | 1.0391 | 0.0019149 | 689.2941 | 0.00043526 | 689.2941 | 1.2436e-06 | 689.2941 | 0.00018609 | 622.7815 | 0.00048116 | 622.7815 | 3.4626e-06 | 622.7815 | 0.00020553
1.0402 | 1.4705e-06 | 1.0402 | 1.4705e-06 | 1.0402 | 0.0019158 | 1.0484 | 1.4718e-06 | 1.0484 | 0.00091517 | 1.0484 | 0.0019228 | 689.2941 | 0.00043526 | 689.2941 | 1.2437e-06 | 689.2941 | 0.00018609 | 622.8353 | 0.00048115 | 622.8353 | 4.8082e-06 | 622.8353 | 0.00020553
1.0494 | 1.4789e-06 | 1.0494 | 1.4789e-06 | 1.0494 | 0.0019236 | 1.0552 | 1.4779e-06 | 1.0552 | 0.00090081 | 1.0552 | 0.0019285 | 689.2941 | 0.00043526 | 689.2941 | 1.2438e-06 | 689.2941 | 0.00018609 | 622.9172 | 0.00048114 | 622.9172 | 6.7451e-06 | 622.9172 | 0.00020553
1.0555 | 1.4844e-06 | 1.0555 | 1.4844e-06 | 1.0555 | 0.0019287 | 1.0574 | 1.4798e-06 | 1.0574 | 0.00089724 | 1.0574 | 0.0019302 | 689.2941 | 0.00043526 | 689.2941 | 1.2441e-06 | 689.2941 | 0.00018609 | 623.031 | 0.00048113 | 623.031 | 9.0432e-06 | 623.031 | 0.00020553
1.0581 | 1.4867e-06 | 1.0581 | 1.4867e-06 | 1.0581 | 0.0019308 | 1.0595 | 1.4817e-06 | 1.0595 | 0.00089426 | 1.0595 | 0.001932 | 689.2941 | 0.00043526 | 689.2941 | 1.2444e-06 | 689.2941 | 0.00018609 | 623.1543 | 0.00048111 | 623.1543 | 1.0958e-05 | 623.1543 | 0.00020553
1.0606 | 1.489e-06 | 1.0606 | 1.489e-06 | 1.0606 | 0.0019329 | 1.0617 | 1.4836e-06 | 1.0617 | 0.00089179 | 1.0617 | 0.0019338 | 689.2941 | 0.00043526 | 689.2941 | 1.2449e-06 | 689.2941 | 0.00018609 | 623.2776 | 0.00048109 | 623.2776 | 1.2331e-05 | 623.2776 | 0.00020552
1.0637 | 1.4917e-06 | 1.0637 | 1.4917e-06 | 1.0637 | 0.0019354 | 1.0662 | 1.4875e-06 | 1.0662 | 0.00088788 | 1.0662 | 0.0019375 | 689.2942 | 0.00043526 | 689.2942 | 1.2458e-06 | 689.2942 | 0.00018609 | 623.4008 | 0.00048107 | 623.4008 | 1.3284e-05 | 623.4008 | 0.00020552
1.0685 | 1.496e-06 | 1.0685 | 1.496e-06 | 1.0685 | 0.0019394 | 1.0721 | 1.4927e-06 | 1.0721 | 0.00088466 | 1.0721 | 0.0019423 | 689.2943 | 0.00043526 | 689.2943 | 1.2472e-06 | 689.2943 | 0.00018609 | 623.5492 | 0.00048105 | 623.5492 | 1.4063e-05 | 623.5492 | 0.00020551
1.0744 | 1.5012e-06 | 1.0744 | 1.5012e-06 | 1.0744 | 0.0019441 | 1.0782 | 1.498e-06 | 1.0782 | 0.00088299 | 1.0782 | 0.0019472 | 689.2945 | 0.00043526 | 689.2945 | 1.2499e-06 | 689.2945 | 0.00018609 | 623.7723 | 0.00048102 | 623.7723 | 1.4812e-05 | 623.7723 | 0.00020549
1.0806 | 1.5067e-06 | 1.0806 | 1.5067e-06 | 1.0806 | 0.0019491 | 1.0844 | 1.5034e-06 | 1.0844 | 0.00088242 | 1.0844 | 0.0019521 | 689.2949 | 0.00043526 | 689.2949 | 1.2568e-06 | 689.2949 | 0.00018609 | 624.0297 | 0.00048098 | 624.0297 | 1.5339e-05 | 624.0297 | 0.00020547
1.0868 | 1.5121e-06 | 1.0868 | 1.5121e-06 | 1.0868 | 0.001954 | 1.0905 | 1.5087e-06 | 1.0905 | 0.00088257 | 1.0905 | 0.001957 | 689.2959 | 0.00043526 | 689.2959 | 1.2737e-06 | 689.2959 | 0.00018609 | 624.2872 | 0.00048095 | 624.2872 | 1.5712e-05 | 624.2872 | 0.00020545
1.093 | 1.5175e-06 | 1.093 | 1.5175e-06 | 1.093 | 0.0019589 | 1.0985 | 1.5155e-06 | 1.0985 | 0.0008834 | 1.0985 | 0.0019633 | 689.2979 | 0.00043526 | 689.2979 | 1.3065e-06 | 689.2979 | 0.00018609 | 624.5446 | 0.00048091 | 624.5446 | 1.6036e-05 | 624.5446 | 0.00020542
1.1015 | 1.5248e-06 | 1.1015 | 1.5248e-06 | 1.1015 | 0.0019656 | 1.1089 | 1.5243e-06 | 1.1089 | 0.00088512 | 1.1089 | 0.0019712 | 689.3014 | 0.00043526 | 689.3014 | 1.3668e-06 | 689.3014 | 0.00018609 | 624.8021 | 0.00048087 | 624.8021 | 1.6342e-05 | 624.8021 | 0.00020539
1.1126 | 1.5343e-06 | 1.1126 | 1.5343e-06 | 1.1126 | 0.0019741 | 1.1215 | 1.5349e-06 | 1.1215 | 0.00088784 | 1.1215 | 0.0019809 | 689.3084 | 0.00043526 | 689.3084 | 1.4877e-06 | 689.3084 | 0.00018609 | 625.1208 | 0.00048083 | 625.1208 | 1.6705e-05 | 625.1208 | 0.00020536
1.1263 | 1.5459e-06 | 1.1263 | 1.5459e-06 | 1.1263 | 0.0019844 | 1.137 | 1.5477e-06 | 1.137 | 0.00089167 | 1.137 | 0.0019923 | 689.3228 | 0.00043526 | 689.3228 | 1.7533e-06 | 689.3228 | 0.00018609 | 625.5791 | 0.00048076 | 625.5791 | 1.72e-05 | 625.5791 | 0.00020532
1.143 | 1.5599e-06 | 1.143 | 1.5599e-06 | 1.143 | 0.0019967 | 1.1567 | 1.5639e-06 | 1.1567 | 0.00089705 | 1.1567 | 0.0020066 | 689.3528 | 0.00043525 | 689.3528 | 2.3503e-06 | 689.3528 | 0.00018609 | 626.2731 | 0.00048067 | 626.2731 | 1.7893e-05 | 626.2731 | 0.00020526
1.1571 | 1.5717e-06 | 1.1571 | 1.5717e-06 | 1.1571 | 0.0020069 | 1.1747 | 1.5801e-06 | 1.1747 | 0.00090233 | 1.1747 | 0.0020192 | 689.4039 | 0.00043524 | 689.4039 | 3.4407e-06 | 689.4039 | 0.00018609 | 627.3304 | 0.00048053 | 627.3304 | 1.8837e-05 | 627.3304 | 0.0002052
1.1745 | 1.5876e-06 | 1.1745 | 1.5876e-06 | 1.1745 | 0.0020191 | 1.1926 | 1.5973e-06 | 1.1926 | 0.00090787 | 1.1926 | 0.0020315 | 689.4754 | 0.00043523 | 689.4754 | 4.9957e-06 | 689.4754 | 0.00018609 | 629.0635 | 0.00048031 | 629.0635 | 2.0146e-05 | 629.0635 | 0.00020516
1.192 | 1.6044e-06 | 1.192 | 1.6044e-06 | 1.192 | 0.0020311 | 1.2106 | 1.6148e-06 | 1.2106 | 0.0009136 | 1.2106 | 0.0020435 | 689.5686 | 0.00043522 | 689.5686 | 6.8775e-06 | 689.5686 | 0.00018609 | 631.9042 | 0.00047996 | 631.9042 | 2.1797e-05 | 631.9042 | 0.00020517
1.2094 | 1.6216e-06 | 1.2094 | 1.6216e-06 | 1.2094 | 0.0020426 | 1.224 | 1.6274e-06 | 1.224 | 0.00091804 | 1.224 | 0.0020521 | 689.6863 | 0.0004352 | 689.6863 | 8.8514e-06 | 689.6863 | 0.00018609 | 635.0079 | 0.00047959 | 635.0079 | 2.3055e-05 | 635.0079 | 0.00020523
1.2226 | 1.6343e-06 | 1.2226 | 1.6343e-06 | 1.2226 | 0.0020512 | 1.2374 | 1.6393e-06 | 1.2374 | 0.00092261 | 1.2374 | 0.0020606 | 689.8138 | 0.00043519 | 689.8138 | 1.045e-05 | 689.8138 | 0.00018608 | 638.1116 | 0.00047925 | 638.1116 | 2.3913e-05 | 638.1116 | 0.0002053
1.2358 | 1.6462e-06 | 1.2358 | 1.6462e-06 | 1.2358 | 0.0020596 | 1.2508 | 1.6505e-06 | 1.2508 | 0.00092727 | 1.2508 | 0.0020689 | 689.9412 | 0.00043517 | 689.9412 | 1.1569e-05 | 689.9412 | 0.00018608 | 641.2152 | 0.00047891 | 641.2152 | 2.4504e-05 | 641.2152 | 0.00020535
1.249 | 1.6574e-06 | 1.249 | 1.6574e-06 | 1.249 | 0.0020678 | 1.2662 | 1.6631e-06 | 1.2662 | 0.00093271 | 1.2662 | 0.0020782 | 690.0761 | 0.00043515 | 690.0761 | 1.2373e-05 | 690.0761 | 0.00018607 | 644.3189 | 0.00047857 | 644.3189 | 2.4915e-05 | 644.3189 | 0.00020539
1.2643 | 1.6701e-06 | 1.2643 | 1.6701e-06 | 1.2643 | 0.0020771 | 1.2816 | 1.6758e-06 | 1.2816 | 0.00093823 | 1.2816 | 0.0020873 | 690.2473 | 0.00043513 | 690.2473 | 1.3044e-05 | 690.2473 | 0.00018606 | 647.4226 | 0.00047825 | 647.4226 | 2.5199e-05 | 647.4226 | 0.00020541
1.2796 | 1.6829e-06 | 1.2796 | 1.6829e-06 | 1.2796 | 0.0020861 | 1.297 | 1.6887e-06 | 1.297 | 0.00094383 | 1.297 | 0.0020961 | 690.4925 | 0.00043509 | 690.4925 | 1.3644e-05 | 690.4925 | 0.00018605 | 651.215 | 0.00047786 | 651.215 | 2.5433e-05 | 651.215 | 0.00020543
1.2949 | 1.696e-06 | 1.2949 | 1.696e-06 | 1.2949 | 0.002095 | 1.3187 | 1.7068e-06 | 1.3187 | 0.00095185 | 1.3187 | 0.0021083 | 690.7632 | 0.00043506 | 690.7632 | 1.4059e-05 | 690.7632 | 0.00018603 | 655.8102 | 0.0004774 | 655.8102 | 2.5606e-05 | 655.8102 | 0.00020544
1.3166 | 1.7142e-06 | 1.3166 | 1.7142e-06 | 1.3166 | 0.0021071 | 1.3405 | 1.724e-06 | 1.3405 | 0.00095997 | 1.3405 | 0.00212 | 691.0339 | 0.00043502 | 691.0339 | 1.4376e-05 | 691.0339 | 0.000186 | 661.18 | 0.00047687 | 661.18 | 2.5715e-05 | 661.18 | 0.00020545
1.3382 | 1.7317e-06 | 1.3382 | 1.7317e-06 | 1.3382 | 0.0021187 | 1.3623 | 1.7405e-06 | 1.3623 | 0.00096814 | 1.3623 | 0.0021313 | 691.3046 | 0.00043498 | 691.3046 | 1.4663e-05 | 691.3046 | 0.00018598 | 667.3663 | 0.00047627 | 667.3663 | 2.5775e-05 | 667.3663 | 0.00020545
1.3598 | 1.7483e-06 | 1.3598 | 1.7483e-06 | 1.3598 | 0.00213 | 1.386 | 1.7582e-06 | 1.386 | 0.00097709 | 1.386 | 0.0021431 | 691.5889 | 0.00043494 | 691.5889 | 1.4951e-05 | 691.5889 | 0.00018595 | 674.6342 | 0.00047559 | 674.6342 | 2.5804e-05 | 674.6342 | 0.00020545
1.3833 | 1.7661e-06 | 1.3833 | 1.7661e-06 | 1.3833 | 0.0021417 | 1.4097 | 1.7758e-06 | 1.4097 | 0.00098607 | 1.4097 | 0.0021544 | 691.9482 | 0.0004349 | 691.9482 | 1.53e-05 | 691.9482 | 0.00018592 | 683.5882 | 0.00047477 | 683.5882 | 2.5816e-05 | 683.5882 | 0.00020544
1.4067 | 1.7838e-06 | 1.4067 | 1.7838e-06 | 1.4067 | 0.002153 | 1.4371 | 1.7958e-06 | 1.4371 | 0.00099644 | 1.4371 | 0.002167 | 692.4584 | 0.00043483 | 692.4584 | 1.5766e-05 | 692.4584 | 0.00018588 | 695.0325 | 0.00047376 | 695.0325 | 2.5819e-05 | 695.0325 | 0.00020544
1.4302 | 1.8013e-06 | 1.4302 | 1.8013e-06 | 1.4302 | 0.0021638 | 1.4646 | 1.8152e-06 | 1.4646 | 0.0010068 | 1.4646 | 0.0021789 | 693.2088 | 0.00043473 | 693.2088 | 1.6395e-05 | 693.2088 | 0.00018583 | 710.3592 | 0.00047247 | 710.3592 | 2.582e-05 | 710.3592 | 0.00020543
1.4608 | 1.8234e-06 | 1.4608 | 1.8234e-06 | 1.4608 | 0.0021773 | 1.4933 | 1.8348e-06 | 1.4933 | 0.0010176 | 1.4933 | 0.0021908 | 694.3361 | 0.00043459 | 694.3361 | 1.7234e-05 | 694.3361 | 0.00018578 | 732.2088 | 0.00047074 | 732.2088 | 2.582e-05 | 732.2088 | 0.00020542
1.4914 | 1.8446e-06 | 1.4914 | 1.8446e-06 | 1.4914 | 0.00219 | 1.5405 | 1.8661e-06 | 1.5405 | 0.0010351 | 1.5405 | 0.0022091 | 696.1764 | 0.00043437 | 696.1764 | 1.8382e-05 | 696.1764 | 0.00018575 | 766.3752 | 0.00046825 | 766.3752 | 2.5821e-05 | 766.3752 | 0.0002054
1.5379 | 1.8759e-06 | 1.5379 | 1.8759e-06 | 1.5379 | 0.0022081 | 1.5877 | 1.8962e-06 | 1.5877 | 0.0010524 | 1.5877 | 0.0022257 | 699.2358 | 0.00043401 | 699.2358 | 1.984e-05 | 699.2358 | 0.00018578 | 827.8291 | 0.00046433 | 827.8291 | 2.5823e-05 | 827.8291 | 0.00020537
1.5844 | 1.9062e-06 | 1.5844 | 1.9062e-06 | 1.5844 | 0.0022246 | 1.6607 | 1.9405e-06 | 1.6607 | 0.0010784 | 1.6607 | 0.0022486 | 702.6847 | 0.00043363 | 702.6847 | 2.0971e-05 | 702.6847 | 0.00018585 | 962.352 | 0.00045743 | 962.352 | 2.5825e-05 | 962.352 | 0.00020531
1.6568 | 1.951e-06 | 1.6568 | 1.951e-06 | 1.6568 | 0.0022475 | 1.7338 | 1.982e-06 | 1.7338 | 0.0011036 | 1.7338 | 0.0022682 | 706.1337 | 0.00043326 | 706.1337 | 2.1729e-05 | 706.1337 | 0.00018592 | 1294.7883 | 0.00044578 | 1294.7883 | 2.5824e-05 | 1294.7883 | 0.00020516
1.7292 | 1.9931e-06 | 1.7292 | 1.9931e-06 | 1.7292 | 0.0022671 | 1.844 | 2.04e-06 | 1.844 | 0.0011396 | 1.844 | 0.0022923 | 709.5827 | 0.00043291 | 709.5827 | 2.2245e-05 | 709.5827 | 0.00018597 | 1695.7558 | 0.00043771 | 1695.7558 | 2.5815e-05 | 1695.7558 | 0.00020499
1.8389 | 2.0521e-06 | 1.8389 | 2.0521e-06 | 1.8389 | 0.0022913 | 1.968 | 2.099e-06 | 1.968 | 0.0011776 | 1.968 | 0.0023121 | 713.0316 | 0.00043256 | 713.0316 | 2.2599e-05 | 713.0316 | 0.000186 | 2096.7232 | 0.00043287 | 2096.7232 | 2.58e-05 | 2096.7232 | 0.00020482
1.9638 | 2.1129e-06 | 1.9638 | 2.1129e-06 | 1.9638 | 0.0023116 | 2.1111 | 2.1593e-06 | 2.1111 | 0.001218 | 2.1111 | 0.0023268 | 716.6916 | 0.0004322 | 716.6916 | 2.2856e-05 | 716.6916 | 0.00018602 | 2510.4602 | 0.00042968 | 2510.4602 | 2.5781e-05 | 2510.4602 | 0.00020465
2.1065 | 2.1749e-06 | 2.1065 | 2.1749e-06 | 2.1065 | 0.0023265 | 2.2541 | 2.2115e-06 | 2.2541 | 0.0012548 | 2.2541 | 0.0023336 | 720.9495 | 0.00043179 | 720.9495 | 2.3053e-05 | 720.9495 | 0.00018603 | 2986.9609 | 0.00042738 | 2986.9609 | 2.5758e-05 | 2986.9609 | 0.00020445
2.2707 | 2.2361e-06 | 2.2707 | 2.2361e-06 | 2.2707 | 0.002334 | 2.3838 | 2.253e-06 | 2.3838 | 0.0012855 | 2.3838 | 0.0023338 | 725.9927 | 0.00043132 | 725.9927 | 2.3193e-05 | 725.9927 | 0.00018604 | 3596.1447 | 0.00042564 | 3596.1447 | 2.5728e-05 | 3596.1447 | 0.0002042
2.4041 | 2.2794e-06 | 2.4041 | 2.2794e-06 | 2.4041 | 0.0023334 | 2.5134 | 2.2891e-06 | 2.5134 | 0.0013137 | 2.5134 | 0.0023291 | 731.9077 | 0.00043078 | 731.9077 | 2.3284e-05 | 731.9077 | 0.00018605 | 3907.8888 | 0.00042576 | 3907.8888 | 2.5779e-05 | 3907.8888 | 0.0002046
2.5376 | 2.3169e-06 | 2.5376 | 2.3169e-06 | 2.5376 | 0.0023278 | 2.6431 | 2.32e-06 | 2.6431 | 0.0013397 | 2.6431 | 0.00232 | 737.8228 | 0.00043025 | 737.8228 | 2.333e-05 | 737.8228 | 0.00018606 | 4219.6328 | 0.0004264 | 4219.6328 | 2.5832e-05 | 4219.6328 | 0.00020501
2.671 | 2.3491e-06 | 2.671 | 2.3491e-06 | 2.671 | 0.0023176 | 2.7917 | 2.3495e-06 | 2.7917 | 0.0013671 | 2.7917 | 0.0023047 | 745.5525 | 0.00042958 | 745.5525 | 2.336e-05 | 745.5525 | 0.00018606 | 4531.3769 | 0.00042719 | 4531.3769 | 2.5884e-05 | 4531.3769 | 0.00020543
2.8204 | 2.3791e-06 | 2.8204 | 2.3791e-06 | 2.8204 | 0.0023013 | 2.8223 | 2.3549e-06 | 2.8223 | 0.0013725 | 2.8223 | 0.002301 | 755.7212 | 0.00042873 | 755.7212 | 2.3376e-05 | 755.7212 | 0.00018606 | 5667.6639 | 0.00043007 | 5667.6639 | 2.6074e-05 | 5667.6639 | 0.00020693
2.8288 | 2.3806e-06 | 2.8288 | 2.3806e-06 | 2.8288 | 0.0023002 | 2.831 | 2.3564e-06 | 2.831 | 0.0013739 | 2.831 | 0.0022999 | 768.6836 | 0.00042769 | 768.6836 | 2.3382e-05 | 768.6836 | 0.00018607 | 5995.5474 | 0.00043094 | 5995.5474 | 2.6129e-05 | 5995.5474 | 0.00020737
2.8325 | 2.3848e-06 | 2.8325 | 2.3848e-06 | 2.8325 | 0.0022997 | 2.8335 | 2.3741e-06 | 2.8335 | 0.0013744 | 2.8335 | 0.0022995 | 785.4643 | 0.00042643 | 785.4643 | 2.3385e-05 | 785.4643 | 0.00018608 | 6046.0665 | 0.00043107 | 6046.0665 | 2.6137e-05 | 6046.0665 | 0.00020744
2.8337 | 2.4025e-06 | 2.8337 | 2.4025e-06 | 2.8337 | 0.0022995 | 2.8346 | 2.4026e-06 | 2.8346 | 0.0013746 | 2.8346 | 0.0022992 | 808.6979 | 0.0004248 | 808.6979 | 2.3388e-05 | 808.6979 | 0.00018609 | 6051.2958 | 0.00043108 | 6051.2958 | 2.6138e-05 | 6051.2958 | 0.00020744
2.8348 | 2.4339e-06 | 2.8348 | 2.4339e-06 | 2.8348 | 0.0022992 | 2.8357 | 2.4352e-06 | 2.8357 | 0.0013748 | 2.8357 | 0.0022989 | 844.7608 | 0.00042252 | 844.7608 | 2.3393e-05 | 844.7608 | 0.0001861 | 6052.2212 | 0.00043109 | 6052.2212 | 2.6138e-05 | 6052.2212 | 0.00020744
2.8361 | 2.4714e-06 | 2.8361 | 2.4714e-06 | 2.8361 | 0.0022989 | 2.8368 | 2.4609e-06 | 2.8368 | 0.0013749 | 2.8368 | 0.0022986 | 910.8624 | 0.00041895 | 910.8624 | 2.3402e-05 | 910.8624 | 0.00018613 | 6061.4749 | 0.00043111 | 6061.4749 | 2.614e-05 | 6061.4749 | 0.00020746
2.8374 | 2.4971e-06 | 2.8374 | 2.4971e-06 | 2.8374 | 0.0022986 | 2.8379 | 2.4766e-06 | 2.8379 | 0.0013751 | 2.8379 | 0.0022984 | 1063.3398 | 0.00041269 | 1063.3398 | 2.3421e-05 | 1063.3398 | 0.00018619 | 6086.9674 | 0.00043118 | 6086.9674 | 2.6144e-05 | 6086.9674 | 0.00020749
2.8387 | 2.5099e-06 | 2.8387 | 2.5099e-06 | 2.8387 | 0.0022983 | 2.8395 | 2.488e-06 | 2.8395 | 0.0013754 | 2.8395 | 0.0022981 | 1421.1157 | 0.00040341 | 1421.1157 | 2.3458e-05 | 1421.1157 | 0.00018635 | 6089.1415 | 0.00043118 | 6089.1415 | 2.6144e-05 | 6089.1415 | 0.00020749
2.8408 | 2.5178e-06 | 2.8408 | 2.5178e-06 | 2.8408 | 0.002298 | 2.8415 | 2.4917e-06 | 2.8415 | 0.0013757 | 2.8415 | 0.0022977 | 1833.0608 | 0.00039792 | 1833.0608 | 2.3492e-05 | 1833.0608 | 0.00018654 | 6098.2203 | 0.0004312 | 6098.2203 | 2.6146e-05 | 6098.2203 | 0.00020751
2.8429 | 2.5185e-06 | 2.8429 | 2.5185e-06 | 2.8429 | 0.0022976 | 2.8434 | 2.492e-06 | 2.8434 | 0.0013761 | 2.8434 | 0.0022974 | 2245.0059 | 0.00039489 | 2245.0059 | 2.3521e-05 | 2245.0059 | 0.00018672 | 6114.127 | 0.00043125 | 6114.127 | 2.6149e-05 | 6114.127 | 0.00020753
2.8451 | 2.5183e-06 | 2.8451 | 2.5183e-06 | 2.8451 | 0.0022972 | 2.8456 | 2.4921e-06 | 2.8456 | 0.0013764 | 2.8456 | 0.0022971 | 2670.0296 | 0.00039312 | 2670.0296 | 2.3549e-05 | 2670.0296 | 0.00018692 | 6145.278 | 0.00043133 | 6145.278 | 2.6154e-05 | 6145.278 | 0.00020757
2.8476 | 2.5186e-06 | 2.8476 | 2.5186e-06 | 2.8476 | 0.0022968 | 2.8486 | 2.4926e-06 | 2.8486 | 0.001377 | 2.8486 | 0.0022965 | 3166.3634 | 0.00039214 | 3166.3634 | 2.3579e-05 | 3166.3634 | 0.00018715 | 6229.2979 | 0.00043154 | 6229.2979 | 2.6168e-05 | 6229.2979 | 0.00020768
2.8523 | 2.5196e-06 | 2.8523 | 2.5196e-06 | 2.8523 | 0.002296 | 2.8553 | 2.4938e-06 | 2.8553 | 0.0013781 | 2.8553 | 0.0022954 | 3811.6249 | 0.0003922 | 3811.6249 | 2.3647e-05 | 3811.6249 | 0.00018768 | 6402.2807 | 0.000432 | 6402.2807 | 2.6197e-05 | 6402.2807 | 0.00020791
2.8639 | 2.5217e-06 | 2.8639 | 2.5217e-06 | 2.8639 | 0.002294 | 2.8725 | 2.4968e-06 | 2.8725 | 0.0013809 | 2.8725 | 0.0022924 | 4539.3643 | 0.00039394 | 4539.3643 | 2.3791e-05 | 4539.3643 | 0.00018881 | 6717.1117 | 0.00043282 | 6717.1117 | 2.6249e-05 | 6717.1117 | 0.00020833
2.8816 | 2.5249e-06 | 2.8816 | 2.5249e-06 | 2.8816 | 0.0022909 | 2.9022 | 2.5014e-06 | 2.9022 | 0.0013858 | 2.9022 | 0.0022871 | 5177.9453 | 0.00039596 | 5177.9453 | 2.3916e-05 | 5177.9453 | 0.00018981 | 7313.1698 | 0.00043433 | 7313.1698 | 2.6345e-05 | 7313.1698 | 0.00020908
2.9117 | 2.5297e-06 | 2.9117 | 2.5297e-06 | 2.9117 | 0.0022855 | 2.9388 | 2.5064e-06 | 2.9388 | 0.0013917 | 2.9388 | 0.0022804 | 5816.5264 | 0.00039797 | 5816.5264 | 2.4042e-05 | 5816.5264 | 0.00019081 | 8530.6659 | 0.0004369 | 8530.6659 | 2.6506e-05 | 8530.6659 | 0.00021036
2.9523 | 2.5353e-06 | 2.9523 | 2.5353e-06 | 2.9523 | 0.0022779 | 2.9738 | 2.5105e-06 | 2.9738 | 0.0013972 | 2.9738 | 0.0022737 | 6774.9247 | 0.00040095 | 6774.9247 | 2.4231e-05 | 6774.9247 | 0.00019231 | 10084.4139 | 0.00044007 | 10084.4139 | 2.6711e-05 | 10084.4139 | 0.00021199
2.9892 | 2.5398e-06 | 2.9892 | 2.5398e-06 | 2.9892 | 0.0022708 | 2.9927 | 2.5125e-06 | 2.9927 | 0.0014001 | 2.9927 | 0.00227 | 7271.7178 | 0.00040237 | 7271.7178 | 2.4318e-05 | 7271.7178 | 0.000193 | 10887.8045 | 0.00044126 | 10887.8045 | 2.6782e-05 | 10887.8045 | 0.00021256
3.0136 | 2.5426e-06 | 3.0136 | 2.5426e-06 | 3.0136 | 0.002266 | 3.0053 | 2.5139e-06 | 3.0053 | 0.0014021 | 3.0053 | 0.0022675 | 7277.0645 | 0.00040238 | 7277.0645 | 2.4318e-05 | 7277.0645 | 0.000193 | 11091.5332 | 0.00044094 | 11091.5332 | 2.6726e-05 | 11091.5332 | 0.00021212
3.0247 | 2.5438e-06 | 3.0247 | 2.5438e-06 | 3.0247 | 0.0022637 | 3.0143 | 2.5148e-06 | 3.0143 | 0.0014035 | 3.0143 | 0.0022657 | 7278.8692 | 0.00040239 | 7278.8692 | 2.4318e-05 | 7278.8692 | 0.000193 | 11295.2619 | 0.00044015 | 11295.2619 | 2.6671e-05 | 11295.2619 | 0.00021168
3.0338 | 2.5448e-06 | 3.0338 | 2.5448e-06 | 3.0338 | 0.0022619 | 3.0202 | 2.5154e-06 | 3.0202 | 0.0014044 | 3.0202 | 0.0022645 | 7279.5449 | 0.00040239 | 7279.5449 | 2.4318e-05 | 7279.5449 | 0.000193 | 11498.9907 | 0.00043918 | 11498.9907 | 2.6616e-05 | 11498.9907 | 0.00021125
3.0398 | 2.5454e-06 | 3.0398 | 2.5454e-06 | 3.0398 | 0.0022606 | 3.0226 | 2.5157e-06 | 3.0226 | 0.0014047 | 3.0226 | 0.0022641 | 7280.2265 | 0.00040239 | 7280.2265 | 2.4318e-05 | 7280.2265 | 0.000193 | 12562.7861 | 0.00043435 | 12562.7861 | 2.6328e-05 | 12562.7861 | 0.00020896
3.0415 | 2.5456e-06 | 3.0415 | 2.5456e-06 | 3.0415 | 0.0022603 | 3.0228 | 2.5157e-06 | 3.0228 | 0.0014047 | 3.0228 | 0.002264 | 7280.8995 | 0.00040239 | 7280.8995 | 2.4318e-05 | 7280.8995 | 0.000193 | 14290.7861 | 0.00042677 | 14290.7861 | 2.586e-05 | 14290.7861 | 0.00020525
3.0419 | 2.5456e-06 | 3.0419 | 2.5456e-06 | 3.0419 | 0.0022602 | 3.0228 | 2.5157e-06 | 3.0228 | 0.0014048 | 3.0228 | 0.002264 | 7281.9141 | 0.0004024 | 7281.9141 | 2.4318e-05 | 7281.9141 | 0.000193 | 14422.8094 | 0.00042644 | 14422.8094 | 2.5864e-05 | 14422.8094 | 0.00020527
3.042 | 2.5456e-06 | 3.042 | 2.5456e-06 | 3.042 | 0.0022602 | 3.0231 | 2.5157e-06 | 3.0231 | 0.0014048 | 3.0231 | 0.0022639 | 7289.6008 | 0.00040241 | 7289.6008 | 2.4319e-05 | 7289.6008 | 0.000193 | 14479.6815 | 0.00042666 | 14479.6815 | 2.5946e-05 | 14479.6815 | 0.00020592
3.0421 | 2.5456e-06 | 3.0421 | 2.5456e-06 | 3.0421 | 0.0022602 | 3.0235 | 2.5158e-06 | 3.0235 | 0.0014049 | 3.0235 | 0.0022639 | 7313.3917 | 0.00040247 | 7313.3917 | 2.432e-05 | 7313.3917 | 0.00019301 | 14536.5536 | 0.00042725 | 14536.5536 | 2.6028e-05 | 14536.5536 | 0.00020656
3.0424 | 2.5456e-06 | 3.0424 | 2.5456e-06 | 3.0424 | 0.0022601 | 3.0241 | 2.5158e-06 | 3.0241 | 0.001405 | 3.0241 | 0.0022637 | 7371.9088 | 0.00040258 | 7371.9088 | 2.4322e-05 | 7371.9088 | 0.00019303 | 14593.4258 | 0.00042813 | 14593.4258 | 2.611e-05 | 14593.4258 | 0.00020721
3.043 | 2.5457e-06 | 3.043 | 2.5457e-06 | 3.043 | 0.00226 | 3.0251 | 2.5159e-06 | 3.0251 | 0.0014051 | 3.0251 | 0.0022635 | 7480.6576 | 0.00040272 | 7480.6576 | 2.4327e-05 | 7480.6576 | 0.00019307 | 14852.9912 | 0.00043346 | 14852.9912 | 2.6482e-05 | 14852.9912 | 0.00021015
3.0436 | 2.5457e-06 | 3.0436 | 2.5457e-06 | 3.0436 | 0.0022599 | 3.0279 | 2.5162e-06 | 3.0279 | 0.0014056 | 3.0279 | 0.002263 | 7517.5826 | 0.00040275 | 7517.5826 | 2.4329e-05 | 7517.5826 | 0.00019309 | 15526.8387 | 0.00044947 | 15526.8387 | 2.7444e-05 | 15526.8387 | 0.00021777
3.0448 | 2.5459e-06 | 3.0448 | 2.5459e-06 | 3.0448 | 0.0022596 | 3.0351 | 2.5169e-06 | 3.0351 | 0.0014068 | 3.0351 | 0.0022615 | 7530.883 | 0.00040276 | 7530.883 | 2.433e-05 | 7530.883 | 0.00019309 | 16471.714 | 0.00047176 | 16471.714 | 2.8787e-05 | 16471.714 | 0.00022842
3.0491 | 2.5462e-06 | 3.0491 | 2.5462e-06 | 3.0491 | 0.0022587 | 3.0488 | 2.518e-06 | 3.0488 | 0.0014091 | 3.0488 | 0.0022587 | 7531.5644 | 0.00040276 | 7531.5644 | 2.433e-05 | 7531.5644 | 0.00019309 | 17621.3148 | 0.00049725 | 17621.3148 | 3.0415e-05 | 17621.3148 | 0.00024132
3.0596 | 2.547e-06 | 3.0596 | 2.547e-06 | 3.0596 | 0.0022565 | 3.0737 | 2.5195e-06 | 3.0737 | 0.0014131 | 3.0737 | 0.0022535 | 7536.8883 | 0.00040276 | 7536.8883 | 2.433e-05 | 7536.8883 | 0.0001931 | 18052.2945 | 0.00050554 | 18052.2945 | 3.0932e-05 | 18052.2945 | 0.00024543
3.0789 | 2.5482e-06 | 3.0789 | 2.5482e-06 | 3.0789 | 0.0022525 | 3.1104 | 2.5212e-06 | 3.1104 | 0.001419 | 3.1104 | 0.0022456 | 7548.797 | 0.00040277 | 7548.797 | 2.4331e-05 | 7548.797 | 0.0001931 | 18114.496 | 0.00050633 | 18114.496 | 3.0909e-05 | 18114.496 | 0.00024527
3.109 | 2.5499e-06 | 3.109 | 2.5499e-06 | 3.109 | 0.002246 | 3.1472 | 2.523e-06 | 3.1472 | 0.0014248 | 3.1472 | 0.0022375 | 7571.9142 | 0.00040279 | 7571.9142 | 2.4332e-05 | 7571.9142 | 0.00019311 | 18176.6975 | 0.00050672 | 18176.6975 | 3.0888e-05 | 18176.6975 | 0.00024512
3.143 | 2.552e-06 | 3.143 | 2.552e-06 | 3.143 | 0.0022385 | 3.1891 | 2.5249e-06 | 3.1891 | 0.0014312 | 3.1891 | 0.002228 | 7614.4627 | 0.00040282 | 7614.4627 | 2.4334e-05 | 7614.4627 | 0.00019312 | 18238.899 | 0.0005068 | 18238.899 | 3.0868e-05 | 18238.899 | 0.00024496
3.1951 | 2.5546e-06 | 3.1951 | 2.5546e-06 | 3.1951 | 0.0022267 | 3.2414 | 2.5261e-06 | 3.2414 | 0.0014389 | 3.2414 | 0.0022157 | 7697.6081 | 0.00040287 | 7697.6081 | 2.4337e-05 | 7697.6081 | 0.00019315 | 18464.5341 | 0.00050611 | 18464.5341 | 3.0795e-05 | 18464.5341 | 0.00024439
3.2473 | 2.5561e-06 | 3.2473 | 2.5561e-06 | 3.2473 | 0.0022145 | 3.2941 | 2.5261e-06 | 3.2941 | 0.0014465 | 3.2941 | 0.002203 | 7868.9109 | 0.00040297 | 7868.9109 | 2.4345e-05 | 7868.9109 | 0.00019322 | 19135.1738 | 0.00050208 | 19135.1738 | 3.0578e-05 | 19135.1738 | 0.0002427
3.3025 | 2.5565e-06 | 3.3025 | 2.5565e-06 | 3.3025 | 0.002201 | 3.3855 | 2.5242e-06 | 3.3855 | 0.001459 | 3.3855 | 0.0021798 | 8219.6943 | 0.00040317 | 8219.6943 | 2.4361e-05 | 8219.6943 | 0.00019335 | 20038.4999 | 0.0004963 | 20038.4999 | 3.0289e-05 | 20038.4999 | 0.00024041
3.3885 | 2.5554e-06 | 3.3885 | 2.5554e-06 | 3.3885 | 0.0021792 | 3.4769 | 2.5199e-06 | 3.4769 | 0.0014708 | 3.4769 | 0.0021555 | 8919.4973 | 0.0004036 | 8919.4973 | 2.4394e-05 | 8919.4973 | 0.0001936 | 20973.2343 | 0.00049132 | 20973.2343 | 2.9991e-05 | 20973.2343 | 0.00023804
3.4803 | 2.5517e-06 | 3.4803 | 2.5517e-06 | 3.4803 | 0.0021547 | 3.6365 | 2.5058e-06 | 3.6365 | 0.0014899 | 3.6365 | 0.0021102 | 10303.2414 | 0.00040456 | 10303.2414 | 2.4458e-05 | 10303.2414 | 0.00019411 | 21181.2466 | 0.00049034 | 21181.2466 | 2.9925e-05 | 21181.2466 | 0.00023752
3.6341 | 2.5393e-06 | 3.6341 | 2.5393e-06 | 3.6341 | 0.0021111 | 3.8135 | 2.4811e-06 | 3.8135 | 0.0015089 | 3.8135 | 0.0020562 | 11019.8661 | 0.00040448 | 11019.8661 | 2.4444e-05 | 11019.8661 | 0.000194 | 21331.8522 | 0.00048963 | 21331.8522 | 2.9877e-05 | 21331.8522 | 0.00023714
3.8224 | 2.5143e-06 | 3.8224 | 2.5143e-06 | 3.8224 | 0.0020535 | 3.8495 | 2.4751e-06 | 3.8495 | 0.0015125 | 3.8495 | 0.0020447 | 11736.4908 | 0.00040279 | 11736.4908 | 2.4323e-05 | 11736.4908 | 0.00019305 | 21499.5663 | 0.00048881 | 21499.5663 | 2.9823e-05 | 21499.5663 | 0.00023671
3.8581 | 2.5085e-06 | 3.8581 | 2.5085e-06 | 3.8581 | 0.0020421 | 3.8579 | 2.4736e-06 | 3.8579 | 0.0015133 | 3.8579 | 0.002042 | 12260.0106 | 0.00040121 | 12260.0106 | 2.4235e-05 | 12260.0106 | 0.00019235 | 21553.2256 | 0.00048854 | 21553.2256 | 2.9806e-05 | 21553.2256 | 0.00023657
3.8615 | 2.5078e-06 | 3.8615 | 2.5078e-06 | 3.8615 | 0.002041 | 3.8609 | 2.473e-06 | 3.8609 | 0.0015136 | 3.8609 | 0.002041 | 12783.5304 | 0.00039972 | 12783.5304 | 2.4147e-05 | 12783.5304 | 0.00019165 | 21588.1125 | 0.00048837 | 21588.1125 | 2.9795e-05 | 21588.1125 | 0.00023649
3.8618 | 2.5078e-06 | 3.8618 | 2.5078e-06 | 3.8618 | 0.0020409 | 3.8615 | 2.4729e-06 | 3.8615 | 0.0015137 | 3.8615 | 0.0020408 | 13613.5356 | 0.00039746 | 13613.5356 | 2.4008e-05 | 13613.5356 | 0.00019055 | 21601.4608 | 0.00048833 | 21601.4608 | 2.9828e-05 | 21601.4608 | 0.00023674
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 14544.2808 | 0.00039553 | 14544.2808 | 2.3893e-05 | 14544.2808 | 0.00018963 | 21605.8469 | 0.00048835 | 21605.8469 | 2.993e-05 | 21605.8469 | 0.00023759
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 14864.2184 | 0.00039573 | 14864.2184 | 2.393e-05 | 14864.2184 | 0.00018992 | 21610.233 | 0.00048842 | 21610.233 | 3.0056e-05 | 21610.233 | 0.00023847
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 15184.1559 | 0.00039638 | 15184.1559 | 2.3967e-05 | 15184.1559 | 0.00019022 | 21614.6191 | 0.00048854 | 21614.6191 | 3.0176e-05 | 21614.6191 | 0.00023934
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 15504.0935 | 0.00039711 | 15504.0935 | 2.4004e-05 | 15504.0935 | 0.00019051 | 21624.1472 | 0.00048898 | 21624.1472 | 3.0426e-05 | 21624.1472 | 0.00024121
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 17020.2986 | 0.00040015 | 17020.2986 | 2.418e-05 | 17020.2986 | 0.00019191 | 21644.4289 | 0.00049067 | 21644.4289 | 3.0941e-05 | 21644.4289 | 0.0002452
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 18748.2986 | 0.00040394 | 18748.2986 | 2.4419e-05 | 18748.2986 | 0.0001938 | 21684.6443 | 0.00049648 | 21684.6443 | 3.1947e-05 | 21684.6443 | 0.0002531
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 20476.2986 | 0.00040849 | 20476.2986 | 2.4709e-05 | 20476.2986 | 0.0001961 | 21755.8157 | 0.00051262 | 21755.8157 | 3.3721e-05 | 21755.8157 | 0.00026703
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 21432.9347 | 0.00041107 | 21432.9347 | 2.4869e-05 | 21432.9347 | 0.00019738 | 21880.8254 | 0.0005513 | 21880.8254 | 3.682e-05 | 21880.8254 | 0.00029135
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 21764.9787 | 0.00041138 | 21764.9787 | 2.4869e-05 | 21764.9787 | 0.00019738 | 22084.44 | 0.00062576 | 22084.44 | 4.1819e-05 | 22084.44 | 0.0003306
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 22097.0228 | 0.00041078 | 22097.0228 | 2.4813e-05 | 22097.0228 | 0.00019694 | 22334.2877 | 0.0007224 | 22334.2877 | 4.7876e-05 | 22334.2877 | 0.00037818
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 22467.817 | 0.00040965 | 22467.817 | 2.4751e-05 | 22467.817 | 0.00019644 | 22640.0847 | 0.00084 | 22640.0847 | 5.519e-05 | 22640.0847 | 0.00043568
3.8619 | 2.5078e-06 | 3.8619 | 2.5078e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 22838.6112 | 0.00040849 | 22838.6112 | 2.4689e-05 | 22838.6112 | 0.00019595 | 22978.8971 | 0.00097132 | 22978.8971 | 6.3189e-05 | 22978.8971 | 0.00049868
3.8619 | 2.508e-06 | 3.8619 | 2.508e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4729e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 23671.6263 | 0.00040612 | 23671.6263 | 2.4549e-05 | 23671.6263 | 0.00019484 | 23344.7564 | 0.0011194 | 23344.7564 | 7.1736e-05 | 23344.7564 | 0.00056612
3.8619 | 2.5084e-06 | 3.8619 | 2.5084e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.473e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 25399.6263 | 0.00040191 | 25399.6263 | 2.4292e-05 | 25399.6263 | 0.0001928 | 23586.2236 | 0.0012223 | 23586.2236 | 7.7336e-05 | 23586.2236 | 0.00061039
3.8619 | 2.509e-06 | 3.8619 | 2.509e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4732e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 25937.6179 | 0.00040162 | 25937.6179 | 2.4289e-05 | 25937.6179 | 0.00019277 | 23875.3699 | 0.0013518 | 23875.3699 | 8.4016e-05 | 23875.3699 | 0.00066323
3.8619 | 2.5098e-06 | 3.8619 | 2.5098e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4736e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 26384.1728 | 0.00040169 | 26384.1728 | 2.4286e-05 | 26384.1728 | 0.00019275 | 24231.0953 | 0.0015173 | 24231.0953 | 9.2194e-05 | 24231.0953 | 0.00072799
3.8619 | 2.5108e-06 | 3.8619 | 2.5108e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4742e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 26830.7276 | 0.00040174 | 26830.7276 | 2.4284e-05 | 26830.7276 | 0.00019273 | 24497.8462 | 0.0016467 | 24497.8462 | 9.831e-05 | 24497.8462 | 0.00077646
3.8619 | 2.5122e-06 | 3.8619 | 2.5122e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4751e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 27732.6072 | 0.00040172 | 27732.6072 | 2.4279e-05 | 27732.6072 | 0.00019269 | 24853.971 | 0.0018268 | 24853.971 | 0.00010646 | 24853.971 | 0.00084106
3.8619 | 2.5144e-06 | 3.8619 | 2.5144e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4761e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28054.494 | 0.00040169 | 28054.494 | 2.4277e-05 | 28054.494 | 0.00019267 | 25033.0296 | 0.0019195 | 25033.0296 | 0.00011054 | 25033.0296 | 0.00087348
3.8619 | 2.5175e-06 | 3.8619 | 2.5175e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4777e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28356.2077 | 0.00040167 | 28356.2077 | 2.4275e-05 | 28356.2077 | 0.00019266 | 25139.0258 | 0.0019746 | 25139.0258 | 0.00011296 | 25139.0258 | 0.00089265
3.8619 | 2.522e-06 | 3.8619 | 2.522e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.48e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28566.6636 | 0.00040165 | 28566.6636 | 2.4274e-05 | 28566.6636 | 0.00019265 | 25211.0939 | 0.0020107 | 25211.0939 | 0.00011423 | 25211.0939 | 0.00090307
3.8619 | 2.5281e-06 | 3.8619 | 2.5281e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4834e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28768.187 | 0.00040163 | 28768.187 | 2.4273e-05 | 28768.187 | 0.00019264 | 25224.438 | 0.0020169 | 25224.438 | 0.00011405 | 25224.438 | 0.00090236
3.8619 | 2.5367e-06 | 3.8619 | 2.5367e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4881e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28793.9352 | 0.00040163 | 28793.9352 | 2.4272e-05 | 28793.9352 | 0.00019264 | 25237.782 | 0.0020226 | 25237.782 | 0.00011387 | 25237.782 | 0.00090157
3.8619 | 2.5494e-06 | 3.8619 | 2.5494e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.4946e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28802.7992 | 0.00040165 | 28802.7992 | 2.4319e-05 | 28802.7992 | 0.00019302 | 25251.1261 | 0.0020277 | 25251.1261 | 0.00011377 | 25251.1261 | 0.00090084
3.8619 | 2.5681e-06 | 3.8619 | 2.5681e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.5038e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28811.6631 | 0.00040178 | 28811.6631 | 2.4474e-05 | 28811.6631 | 0.00019424 | 25266.6002 | 0.002033 | 25266.6002 | 0.00011365 | 25266.6002 | 0.00089998
3.8619 | 2.5956e-06 | 3.8619 | 2.5956e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.5176e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28818.2859 | 0.00040197 | 28818.2859 | 2.4599e-05 | 28818.2859 | 0.00019516 | 25297.2885 | 0.0020418 | 25297.2885 | 0.00011341 | 25297.2885 | 0.00089825
3.8619 | 2.6365e-06 | 3.8619 | 2.6365e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.5377e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28824.9087 | 0.00040225 | 28824.9087 | 2.4717e-05 | 28824.9087 | 0.00019607 | 25360.2953 | 0.0020542 | 25360.2953 | 0.00011291 | 25360.2953 | 0.00089465
3.8619 | 2.6987e-06 | 3.8619 | 2.6987e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.5673e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28836.5338 | 0.00040292 | 28836.5338 | 2.4922e-05 | 28836.5338 | 0.00019767 | 25466.4455 | 0.0020625 | 25466.4455 | 0.00011207 | 25466.4455 | 0.00088847
3.8619 | 2.7967e-06 | 3.8619 | 2.7967e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.6114e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28868.3777 | 0.00040586 | 28868.3777 | 2.548e-05 | 28868.3777 | 0.00020206 | 25610.6122 | 0.0020582 | 25610.6122 | 0.00011092 | 25610.6122 | 0.00087989
3.8619 | 2.9567e-06 | 3.8619 | 2.9567e-06 | 3.8619 | 0.0020409 | 3.8617 | 2.6796e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 28965.2832 | 0.00042139 | 28965.2832 | 2.7168e-05 | 28965.2832 | 0.00021536 | 25771.0708 | 0.0020414 | 25771.0708 | 0.00010963 | 25771.0708 | 0.00087014
3.862 | 3.2264e-06 | 3.862 | 3.2264e-06 | 3.862 | 0.0020409 | 3.8617 | 2.7874e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 29155.2801 | 0.00046641 | 29155.2801 | 3.0458e-05 | 29155.2801 | 0.00024129 | 25931.5294 | 0.0020181 | 25931.5294 | 0.00010834 | 25931.5294 | 0.00086026
3.862 | 3.6918e-06 | 3.862 | 3.6918e-06 | 3.862 | 0.002041 | 3.8617 | 2.9642e-06 | 3.8617 | 0.0015137 | 3.8617 | 0.0020408 | 29398.5398 | 0.00053379 | 29398.5398 | 3.463e-05 | 29398.5398 | 0.00027417 | 26126.758 | 0.0019858 | 26126.758 | 0.00010677 | 26126.758 | 0.0008481
3.8621 | 4.2607e-06 | 3.8621 | 4.2607e-06 | 3.8621 | 0.002041 | 3.8618 | 3.2653e-06 | 3.8618 | 0.0015137 | 3.8618 | 0.0020408 | 29676.1658 | 0.00061044 | 29676.1658 | 3.934e-05 | 29676.1658 | 0.00031127 | 26345.8538 | 0.0019467 | 26345.8538 | 0.00010501 | 26345.8538 | 0.00083433
3.8622 | 5.1841e-06 | 3.8622 | 5.1841e-06 | 3.8622 | 0.0020411 | 3.8618 | 3.789e-06 | 3.8618 | 0.0015137 | 3.8618 | 0.0020409 | 30041.6864 | 0.0007071 | 30041.6864 | 4.5464e-05 | 30041.6864 | 0.00035953 | 26584.7712 | 0.0019024 | 26584.7712 | 0.00010308 | 26584.7712 | 0.00081922
3.8624 | 7.0874e-06 | 3.8624 | 7.0874e-06 | 3.8624 | 0.0020413 | 3.8619 | 4.4355e-06 | 3.8619 | 0.0015137 | 3.8619 | 0.002041 | 30572.9222 | 0.00084509 | 30572.9222 | 5.4232e-05 | 30572.9222 | 0.00042867 | 26849.4521 | 0.0018525 | 26849.4521 | 0.00010095 | 26849.4521 | 0.0008024
3.8627 | 9.7234e-06 | 3.8627 | 9.7234e-06 | 3.8627 | 0.0020416 | 3.862 | 5.5011e-06 | 3.862 | 0.0015137 | 3.862 | 0.0020411 | 31104.1579 | 0.00098699 | 31104.1579 | 6.2875e-05 | 31104.1579 | 0.00049693 | 27150.8588 | 0.0017959 | 27150.8588 | 9.8519e-05 | 27150.8588 | 0.00078319
3.8633 | 1.4038e-05 | 3.8633 | 1.4038e-05 | 3.8633 | 0.002042 | 3.8623 | 7.6349e-06 | 3.8623 | 0.0015138 | 3.8623 | 0.0020413 | 31635.3937 | 0.0011378 | 31635.3937 | 7.1432e-05 | 31635.3937 | 0.00056459 | 27502.1885 | 0.0017309 | 27502.1885 | 9.5683e-05 | 27502.1885 | 0.00076073
3.864 | 1.9419e-05 | 3.864 | 1.9419e-05 | 3.864 | 0.0020426 | 3.8626 | 1.0366e-05 | 3.8626 | 0.0015138 | 3.8626 | 0.0020416 | 31986.0093 | 0.0012433 | 31986.0093 | 7.704e-05 | 31986.0093 | 0.00060901 | 27921.7329 | 0.001654 | 27921.7329 | 9.2292e-05 | 27921.7329 | 0.00073383
3.8648 | 2.4993e-05 | 3.8648 | 2.4993e-05 | 3.8648 | 0.0020432 | 3.8632 | 1.4757e-05 | 3.8632 | 0.0015138 | 3.8632 | 0.002042 | 32393.6532 | 0.0013708 | 32393.6532 | 8.3535e-05 | 32393.6532 | 0.00066047 | 28416.6357 | 0.0015647 | 28416.6357 | 8.8286e-05 | 28416.6357 | 0.00070204
3.8657 | 3.0297e-05 | 3.8657 | 3.0297e-05 | 3.8657 | 0.0020439 | 3.8639 | 2.0243e-05 | 3.8639 | 0.0015139 | 3.8639 | 0.0020426 | 32446.4895 | 0.0013869 | 32446.4895 | 8.41e-05 | 32446.4895 | 0.00066523 | 28609.3031 | 0.0015306 | 28609.3031 | 8.6724e-05 | 28609.3031 | 0.00068964
3.8667 | 3.4975e-05 | 3.8667 | 3.4975e-05 | 3.8667 | 0.0020445 | 3.8647 | 2.5168e-05 | 3.8647 | 0.001514 | 3.8647 | 0.0020432 | 32499.3259 | 0.0014021 | 32499.3259 | 8.4657e-05 | 32499.3259 | 0.00066972 | 28751.2332 | 0.0015057 | 28751.2332 | 8.5574e-05 | 28751.2332 | 0.0006805
3.8676 | 3.9106e-05 | 3.8676 | 3.9106e-05 | 3.8676 | 0.0020451 | 3.8655 | 2.9592e-05 | 3.8655 | 0.0015141 | 3.8655 | 0.0020437 | 32552.1622 | 0.0014163 | 32552.1622 | 8.5222e-05 | 32552.1622 | 0.00067421 | 28801.0057 | 0.0014971 | 28801.0057 | 8.5194e-05 | 28801.0057 | 0.00067747
3.8686 | 4.3419e-05 | 3.8686 | 4.3419e-05 | 3.8686 | 0.0020457 | 3.8663 | 3.3563e-05 | 3.8663 | 0.0015141 | 3.8663 | 0.0020443 | 32638.9363 | 0.0014385 | 32638.9363 | 8.6142e-05 | 32638.9363 | 0.00068157 | 28812.9489 | 0.0014952 | 28812.9489 | 8.5405e-05 | 28812.9489 | 0.00067871
3.8697 | 4.7143e-05 | 3.8697 | 4.7143e-05 | 3.8697 | 0.0020464 | 3.8671 | 3.7421e-05 | 3.8671 | 0.0015142 | 3.8671 | 0.0020448 | 32914.4437 | 0.0015045 | 32914.4437 | 8.9062e-05 | 32914.4437 | 0.00070489 | 28824.8921 | 0.0014937 | 28824.8921 | 8.5628e-05 | 28824.8921 | 0.00068001
3.871 | 5.0936e-05 | 3.871 | 5.0936e-05 | 3.871 | 0.0020472 | 3.8681 | 4.1656e-05 | 3.8681 | 0.0015143 | 3.8681 | 0.0020455 | 33325.1687 | 0.0015986 | 33325.1687 | 9.3411e-05 | 33325.1687 | 0.00073954 | 28836.8354 | 0.0014924 | 28836.8354 | 8.5803e-05 | 28836.8354 | 0.00068127
3.8723 | 5.4124e-05 | 3.8723 | 5.4124e-05 | 3.8723 | 0.0020479 | 3.8694 | 4.6057e-05 | 3.8694 | 0.0015144 | 3.8694 | 0.0020462 | 33736.8955 | 0.0016928 | 33736.8955 | 9.7769e-05 | 33736.8955 | 0.00077416 | 28853.1366 | 0.0014912 | 28853.1366 | 8.6024e-05 | 28853.1366 | 0.00068299
3.8736 | 5.6804e-05 | 3.8736 | 5.6804e-05 | 3.8736 | 0.0020486 | 3.8707 | 5.0021e-05 | 3.8707 | 0.0015146 | 3.8707 | 0.002047 | 34150.2159 | 0.0017895 | 34150.2159 | 0.00010214 | 34150.2159 | 0.00080885 | 28884.9059 | 0.0014903 | 28884.9059 | 8.6463e-05 | 28884.9059 | 0.00068636
3.8752 | 5.9556e-05 | 3.8752 | 5.9556e-05 | 3.8752 | 0.0020495 | 3.8722 | 5.3469e-05 | 3.8722 | 0.0015147 | 3.8722 | 0.0020478 | 34628.9492 | 0.0019018 | 34628.9492 | 0.00010719 | 34628.9492 | 0.00084894 | 28952.3028 | 0.0014929 | 28952.3028 | 8.7401e-05 | 28952.3028 | 0.00069351
3.8771 | 6.2075e-05 | 3.8771 | 6.2075e-05 | 3.8771 | 0.0020505 | 3.8737 | 5.6498e-05 | 3.8737 | 0.0015149 | 3.8737 | 0.0020487 | 35229.3045 | 0.0020443 | 35229.3045 | 0.00011351 | 35229.3045 | 0.00089913 | 29097.2438 | 0.001512 | 29097.2438 | 8.9409e-05 | 29097.2438 | 0.00070895
3.8789 | 6.4052e-05 | 3.8789 | 6.4052e-05 | 3.8789 | 0.0020514 | 3.8752 | 5.8974e-05 | 3.8752 | 0.001515 | 3.8752 | 0.0020495 | 35676.7623 | 0.0021525 | 35676.7623 | 0.00011822 | 35676.7623 | 0.0009365 | 29270.9728 | 0.0015494 | 29270.9728 | 9.1806e-05 | 29270.9728 | 0.00072752
3.8808 | 6.5606e-05 | 3.8808 | 6.5606e-05 | 3.8808 | 0.0020523 | 3.8769 | 6.1296e-05 | 3.8769 | 0.0015152 | 3.8769 | 0.0020504 | 36049.9382 | 0.0022421 | 36049.9382 | 0.000122 | 36049.9382 | 0.00096652 | 29457.2768 | 0.0015978 | 29457.2768 | 9.4367e-05 | 29457.2768 | 0.0007475
3.883 | 6.707e-05 | 3.883 | 6.707e-05 | 3.883 | 0.0020535 | 3.8789 | 6.3355e-05 | 3.8789 | 0.0015154 | 3.8789 | 0.0020514 | 36199.2576 | 0.002275 | 36199.2576 | 0.00012312 | 36199.2576 | 0.00097564 | 29670.8577 | 0.001658 | 29670.8577 | 9.7296e-05 | 29670.8577 | 0.00077046
3.8853 | 6.8172e-05 | 3.8853 | 6.8172e-05 | 3.8853 | 0.0020546 | 3.8809 | 6.4946e-05 | 3.8809 | 0.0015156 | 3.8809 | 0.0020524 | 36348.5771 | 0.0023049 | 36348.5771 | 0.00012426 | 36348.5771 | 0.00098474 | 29897.2586 | 0.0017249 | 29897.2586 | 0.00010039 | 29897.2586 | 0.00079485
3.888 | 6.9175e-05 | 3.888 | 6.9175e-05 | 3.888 | 0.0020559 | 3.8832 | 6.6351e-05 | 3.8832 | 0.0015158 | 3.8832 | 0.0020536 | 36497.8965 | 0.0023329 | 36497.8965 | 0.0001254 | 36497.8965 | 0.00099382 | 30139.7855 | 0.0017989 | 30139.7855 | 0.00010371 | 30139.7855 | 0.00082101
3.8908 | 6.9897e-05 | 3.8908 | 6.9897e-05 | 3.8908 | 0.0020573 | 3.8858 | 6.7531e-05 | 3.8858 | 0.001516 | 3.8858 | 0.0020549 | 36745.3765 | 0.0023773 | 36745.3765 | 0.00012728 | 36745.3765 | 0.0010088 | 30411.8247 | 0.0018829 | 30411.8247 | 0.00010742 | 30411.8247 | 0.00085035
3.8942 | 7.0539e-05 | 3.8942 | 7.0539e-05 | 3.8942 | 0.0020589 | 3.8884 | 6.8387e-05 | 3.8884 | 0.0015163 | 3.8884 | 0.0020561 | 37027.501 | 0.0024267 | 37027.501 | 0.00012943 | 37027.501 | 0.0010259 | 30736.2465 | 0.0019843 | 30736.2465 | 0.00011184 | 30736.2465 | 0.00088535
3.8976 | 7.0989e-05 | 3.8976 | 7.0989e-05 | 3.8976 | 0.0020606 | 3.8915 | 6.9127e-05 | 3.8915 | 0.0015166 | 3.8915 | 0.0020576 | 37479.922 | 0.0025055 | 37479.922 | 0.00013287 | 37479.922 | 0.0010532 | 31102.5994 | 0.0021004 | 31102.5994 | 0.00011682 | 31102.5994 | 0.00092488
3.9021 | 7.1407e-05 | 3.9021 | 7.1407e-05 | 3.9021 | 0.0020627 | 3.8952 | 6.9732e-05 | 3.8952 | 0.0015169 | 3.8952 | 0.0020594 | 37877.9223 | 0.0025747 | 37877.9223 | 0.00013589 | 37877.9223 | 0.0010772 | 31541.2423 | 0.0022413 | 31541.2423 | 0.00012282 | 31541.2423 | 0.00097218
3.9077 | 7.1779e-05 | 3.9077 | 7.1779e-05 | 3.9077 | 0.0020654 | 3.8989 | 7.0151e-05 | 3.8989 | 0.0015173 | 3.8989 | 0.0020612 | 38273.373 | 0.0026434 | 38273.373 | 0.0001389 | 38273.373 | 0.0011011 | 31888.9741 | 0.0023532 | 31888.9741 | 0.00012751 | 31888.9741 | 0.0010097
3.9144 | 7.2119e-05 | 3.9144 | 7.2119e-05 | 3.9144 | 0.0020685 | 3.9036 | 7.0531e-05 | 3.9036 | 0.0015177 | 3.9036 | 0.0020634 | 38576.0735 | 0.0026959 | 38576.0735 | 0.0001412 | 38576.0735 | 0.0011193 | 32102.0477 | 0.002421 | 32102.0477 | 0.00013039 | 32102.0477 | 0.0010326
3.9226 | 7.2472e-05 | 3.9226 | 7.2472e-05 | 3.9226 | 0.0020724 | 3.9094 | 7.088e-05 | 3.9094 | 0.0015183 | 3.9094 | 0.0020662 | 38952.484 | 0.0027608 | 38952.484 | 0.00014405 | 38952.484 | 0.001142 | 32438.6939 | 0.0025269 | 32438.6939 | 0.00013492 | 32438.6939 | 0.0010685
3.933 | 7.2904e-05 | 3.933 | 7.2904e-05 | 3.933 | 0.0020773 | 3.9166 | 7.1216e-05 | 3.9166 | 0.0015189 | 3.9166 | 0.0020696 | 39450.842 | 0.0028451 | 39450.842 | 0.00014783 | 39450.842 | 0.001172 | 32662.5882 | 0.0025949 | 32662.5882 | 0.0001377 | 32662.5882 | 0.0010907
3.9393 | 7.3164e-05 | 3.9393 | 7.3164e-05 | 3.9393 | 0.0020802 | 3.9255 | 7.1585e-05 | 3.9255 | 0.0015198 | 3.9255 | 0.0020738 | 39736.1301 | 0.002889 | 39736.1301 | 0.00014965 | 39736.1301 | 0.0011866 | 32904.6297 | 0.0026663 | 32904.6297 | 0.00014073 | 32904.6297 | 0.0011147
3.9457 | 7.3443e-05 | 3.9457 | 7.3443e-05 | 3.9457 | 0.0020833 | 3.937 | 7.2056e-05 | 3.937 | 0.0015208 | 3.937 | 0.0020792 | 40021.4181 | 0.0029259 | 40021.4181 | 0.00015111 | 40021.4181 | 0.0011983 | 33159.2107 | 0.0027401 | 33159.2107 | 0.00014391 | 33159.2107 | 0.00114
3.9597 | 7.4079e-05 | 3.9597 | 7.4079e-05 | 3.9597 | 0.0020898 | 3.9531 | 7.2747e-05 | 3.9531 | 0.0015222 | 3.9531 | 0.0020867 | 40330.3213 | 0.0029613 | 40330.3213 | 0.0001527 | 40330.3213 | 0.001211 | 33348.5369 | 0.0027945 | 33348.5369 | 0.00014627 | 33348.5369 | 0.0011587
3.9804 | 7.5074e-05 | 3.9804 | 7.5074e-05 | 3.9804 | 0.0020993 | 3.9734 | 7.3683e-05 | 3.9734 | 0.001524 | 3.9734 | 0.0020961 | 40639.2246 | 0.002995 | 40639.2246 | 0.00015428 | 40639.2246 | 0.0012236 | 33613.3893 | 0.002869 | 33613.3893 | 0.00014957 | 33613.3893 | 0.001185
3.9972 | 7.5903e-05 | 3.9972 | 7.5903e-05 | 3.9972 | 0.002107 | 3.9902 | 7.4496e-05 | 3.9902 | 0.0015255 | 3.9902 | 0.0021038 | 40950.1859 | 0.0030288 | 40950.1859 | 0.00015588 | 40950.1859 | 0.0012363 | 33770.0545 | 0.0029125 | 33770.0545 | 0.00015152 | 33770.0545 | 0.0012004
4.0139 | 7.672e-05 | 4.0139 | 7.672e-05 | 4.0139 | 0.0021146 | 4.007 | 7.5311e-05 | 4.007 | 0.0015269 | 4.007 | 0.0021115 | 41329.767 | 0.0030697 | 41329.767 | 0.00015782 | 41329.767 | 0.0012517 | 34017.1665 | 0.0029803 | 34017.1665 | 0.0001546 | 34017.1665 | 0.0012249
4.0307 | 7.7506e-05 | 4.0307 | 7.7506e-05 | 4.0307 | 0.0021222 | 4.0143 | 7.5661e-05 | 4.0143 | 0.0015276 | 4.0143 | 0.0021148 | 41750.2716 | 0.0031147 | 41750.2716 | 0.00015998 | 41750.2716 | 0.0012688 | 34200.0901 | 0.0030301 | 34200.0901 | 0.00015687 | 34200.0901 | 0.0012429
4.0574 | 7.8692e-05 | 4.0574 | 7.8692e-05 | 4.0574 | 0.0021342 | 4.028 | 7.6296e-05 | 4.028 | 0.0015288 | 4.028 | 0.002121 | 42083.0445 | 0.0031499 | 42083.0445 | 0.00016168 | 42083.0445 | 0.0012824 | 34431.0062 | 0.0030923 | 34431.0062 | 0.00015975 | 34431.0062 | 0.0012658
4.063 | 7.8941e-05 | 4.063 | 7.8941e-05 | 4.063 | 0.0021367 | 4.0518 | 7.7341e-05 | 4.0518 | 0.0015307 | 4.0518 | 0.0021317 | 42506.2026 | 0.0031942 | 42506.2026 | 0.00016385 | 42506.2026 | 0.0012996 | 34586.9592 | 0.0031339 | 34586.9592 | 0.00016169 | 34586.9592 | 0.0012812
4.0686 | 7.921e-05 | 4.0686 | 7.921e-05 | 4.0686 | 0.0021392 | 4.0756 | 7.8347e-05 | 4.0756 | 0.0015327 | 4.0756 | 0.0021423 | 43129.2506 | 0.0032574 | 43129.2506 | 0.00016704 | 43129.2506 | 0.0013249 | 34772.8398 | 0.0031829 | 34772.8398 | 0.00016401 | 34772.8398 | 0.0012995
4.0739 | 7.9481e-05 | 4.0739 | 7.9481e-05 | 4.0739 | 0.0021415 | 4.0993 | 7.9358e-05 | 4.0993 | 0.0015346 | 4.0993 | 0.0021528 | 43301.0353 | 0.0032711 | 43301.0353 | 0.00016749 | 43301.0353 | 0.0013287 | 34932.2991 | 0.0032244 | 34932.2991 | 0.00016599 | 34932.2991 | 0.0013153
4.0792 | 7.9763e-05 | 4.0792 | 7.9763e-05 | 4.0792 | 0.0021439 | 4.1231 | 8.0404e-05 | 4.1231 | 0.0015364 | 4.1231 | 0.0021632 | 43472.82 | 0.0032795 | 43472.82 | 0.00016767 | 43472.82 | 0.0013303 | 35117.4519 | 0.003272 | 35117.4519 | 0.00016829 | 35117.4519 | 0.0013336
4.094 | 8.0578e-05 | 4.094 | 8.0578e-05 | 4.094 | 0.0021504 | 4.1394 | 8.1154e-05 | 4.1394 | 0.0015377 | 4.1394 | 0.0021702 | 43698.2665 | 0.0032857 | 43698.2665 | 0.00016792 | 43698.2665 | 0.0013324 | 35439.5759 | 0.0033518 | 35439.5759 | 0.0001723 | 35439.5759 | 0.0013654
4.1253 | 8.2401e-05 | 4.1253 | 8.2401e-05 | 4.1253 | 0.0021641 | 4.1429 | 8.1326e-05 | 4.1429 | 0.0015379 | 4.1429 | 0.0021717 | 43923.7131 | 0.0032897 | 43923.7131 | 0.00016817 | 43923.7131 | 0.0013344 | 35597.7755 | 0.0033901 | 35597.7755 | 0.00017426 | 35597.7755 | 0.001381
4.1525 | 8.4046e-05 | 4.1525 | 8.4046e-05 | 4.1525 | 0.0021758 | 4.1463 | 8.1507e-05 | 4.1463 | 0.0015382 | 4.1463 | 0.0021732 | 44252.8484 | 0.0032953 | 44252.8484 | 0.00016852 | 44252.8484 | 0.0013373 | 35736.125 | 0.0034233 | 35736.125 | 0.00017598 | 35736.125 | 0.0013946
4.1797 | 8.5705e-05 | 4.1797 | 8.5705e-05 | 4.1797 | 0.0021874 | 4.1498 | 8.1696e-05 | 4.1498 | 0.0015385 | 4.1498 | 0.0021747 | 44704.6981 | 0.0033033 | 44704.6981 | 0.000169 | 44704.6981 | 0.0013411 | 35889.7225 | 0.0034597 | 35889.7225 | 0.00017789 | 35889.7225 | 0.0014098
4.2068 | 8.7351e-05 | 4.2068 | 8.7351e-05 | 4.2068 | 0.0021989 | 4.1664 | 8.2638e-05 | 4.1664 | 0.0015398 | 4.1664 | 0.0021818 | 45252.5978 | 0.0033135 | 45252.5978 | 0.00016959 | 45252.5978 | 0.0013458 | 36055.6601 | 0.0034998 | 36055.6601 | 0.00018012 | 36055.6601 | 0.0014274
4.2413 | 8.9422e-05 | 4.2413 | 8.9422e-05 | 4.2413 | 0.0022132 | 4.1927 | 8.4158e-05 | 4.1927 | 0.0015419 | 4.1927 | 0.0021929 | 45895.2812 | 0.0033259 | 45895.2812 | 0.00017027 | 45895.2812 | 0.0013512 | 36193.05 | 0.0035353 | 36193.05 | 0.00018223 | 36193.05 | 0.001444
4.2758 | 9.1504e-05 | 4.2758 | 9.1504e-05 | 4.2758 | 0.0022274 | 4.2238 | 8.5946e-05 | 4.2238 | 0.0015446 | 4.2238 | 0.002206 | 46702.2296 | 0.0033419 | 46702.2296 | 0.00017113 | 46702.2296 | 0.001358 | 36309.2632 | 0.0035666 | 36309.2632 | 0.000184 | 36309.2632 | 0.001458
4.3103 | 9.3627e-05 | 4.3103 | 9.3627e-05 | 4.3103 | 0.0022414 | 4.2607 | 8.8067e-05 | 4.2607 | 0.0015479 | 4.2607 | 0.0022213 | 46845.7793 | 0.0033418 | 46845.7793 | 0.00017088 | 46845.7793 | 0.0013563 | 36443.0732 | 0.0036032 | 36443.0732 | 0.00018604 | 36443.0732 | 0.0014742
4.3554 | 9.6447e-05 | 4.3554 | 9.6447e-05 | 4.3554 | 0.0022594 | 4.2975 | 9.0231e-05 | 4.2975 | 0.0015512 | 4.2975 | 0.0022363 | 46989.329 | 0.0033328 | 46989.329 | 0.00016978 | 46989.329 | 0.0013481 | 36544.5088 | 0.0036308 | 36544.5088 | 0.00018759 | 36544.5088 | 0.0014865
4.3851 | 9.8319e-05 | 4.3851 | 9.8319e-05 | 4.3851 | 0.0022711 | 4.335 | 9.2482e-05 | 4.335 | 0.0015547 | 4.335 | 0.0022514 | 47091.1259 | 0.0033216 | 47091.1259 | 0.00016904 | 47091.1259 | 0.0013423 | 36664.8175 | 0.0036632 | 36664.8175 | 0.00018943 | 36664.8175 | 0.001501
4.392 | 9.8748e-05 | 4.392 | 9.8748e-05 | 4.392 | 0.0022738 | 4.3642 | 9.4253e-05 | 4.3642 | 0.0015573 | 4.3642 | 0.0022629 | 47192.9229 | 0.0033082 | 47192.9229 | 0.00016829 | 47192.9229 | 0.0013364 | 36695.8986 | 0.0036714 | 36695.8986 | 0.00018991 | 36695.8986 | 0.0015048
4.4035 | 9.9449e-05 | 4.4035 | 9.9449e-05 | 4.4035 | 0.0022783 | 4.3743 | 9.4863e-05 | 4.3743 | 0.0015583 | 4.3743 | 0.0022669 | 47327.0137 | 0.0032891 | 47327.0137 | 0.0001673 | 47327.0137 | 0.0013287 | 36702.4214 | 0.0036732 | 36702.4214 | 0.00019001 | 36702.4214 | 0.0015056
4.4188 | 0.00010037 | 4.4188 | 0.00010037 | 4.4188 | 0.0022842 | 4.3873 | 9.5618e-05 | 4.3873 | 0.0015594 | 4.3873 | 0.002272 | 47549.555 | 0.0032563 | 47549.555 | 0.00016565 | 47549.555 | 0.0013157 | 36704.6408 | 0.0036737 | 36704.6408 | 0.00019004 | 36704.6408 | 0.0015059
4.4341 | 0.00010127 | 4.4341 | 0.00010127 | 4.4341 | 0.0022901 | 4.4008 | 9.6388e-05 | 4.4008 | 0.0015606 | 4.4008 | 0.0022773 | 47864.7149 | 0.0032091 | 47864.7149 | 0.0001633 | 47864.7149 | 0.0012972 | 36704.9888 | 0.0036738 | 36704.9888 | 0.00019005 | 36704.9888 | 0.0015059
4.4505 | 0.00010224 | 4.4505 | 0.00010224 | 4.4505 | 0.0022964 | 4.4143 | 9.7149e-05 | 4.4143 | 0.0015618 | 4.4143 | 0.0022825 | 48244.0434 | 0.0031522 | 48244.0434 | 0.00016048 | 48244.0434 | 0.0012749 | 36705.1142 | 0.0036739 | 36705.1142 | 0.00019005 | 36705.1142 | 0.0015059
4.4756 | 0.00010372 | 4.4756 | 0.00010372 | 4.4756 | 0.0023059 | 4.4361 | 9.8372e-05 | 4.4361 | 0.0015637 | 4.4361 | 0.0022909 | 48423.1877 | 0.0031255 | 48423.1877 | 0.00015915 | 48423.1877 | 0.0012644 | 36705.2563 | 0.0036739 | 36705.2563 | 0.00019005 | 36705.2563 | 0.0015059
4.5222 | 0.00010646 | 4.5222 | 0.00010646 | 4.5222 | 0.0023233 | 4.4476 | 9.9013e-05 | 4.4476 | 0.0015647 | 4.4476 | 0.0022953 | 48663.2037 | 0.0030891 | 48663.2037 | 0.00015736 | 48663.2037 | 0.0012502 | 36705.3476 | 0.0036739 | 36705.3476 | 0.00019005 | 36705.3476 | 0.0015059
4.5687 | 0.00010917 | 4.5687 | 0.00010917 | 4.5687 | 0.0023404 | 4.4648 | 9.9976e-05 | 4.4648 | 0.0015662 | 4.4648 | 0.0023018 | 48870.0119 | 0.0030574 | 48870.0119 | 0.00015582 | 48870.0119 | 0.001238 | 36705.439 | 0.0036739 | 36705.439 | 0.00019005 | 36705.439 | 0.0015059
4.6248 | 0.00011238 | 4.6248 | 0.00011238 | 4.6248 | 0.0023606 | 4.4971 | 0.00010179 | 4.4971 | 0.001569 | 4.4971 | 0.002314 | 49225.3406 | 0.0030021 | 49225.3406 | 0.00015317 | 49225.3406 | 0.0012169 | 36705.5509 | 0.003674 | 36705.5509 | 0.00019005 | 36705.5509 | 0.0015059
4.718 | 0.00011762 | 4.718 | 0.00011762 | 4.718 | 0.0023931 | 4.531 | 0.00010367 | 4.531 | 0.0015718 | 4.531 | 0.0023266 | 49494.0639 | 0.0029599 | 49494.0639 | 0.00015116 | 49494.0639 | 0.001201 | 36705.7934 | 0.003674 | 36705.7934 | 0.00019004 | 36705.7934 | 0.001506
4.7795 | 0.00012102 | 4.7795 | 0.00012102 | 4.7795 | 0.0024139 | 4.5742 | 0.00010604 | 4.5742 | 0.0015754 | 4.5742 | 0.0023424 | 49871.4041 | 0.0029 | 49871.4041 | 0.00014835 | 49871.4041 | 0.0011787 | 36705.9534 | 0.0036741 | 36705.9534 | 0.00019003 | 36705.9534 | 0.001506
4.8016 | 0.00012223 | 4.8016 | 0.00012223 | 4.8016 | 0.0024212 | 4.6328 | 0.00010922 | 4.6328 | 0.0015801 | 4.6328 | 0.0023634 | 50201.7225 | 0.002847 | 50201.7225 | 0.00014589 | 50201.7225 | 0.0011592 | 36706.1134 | 0.0036741 | 36706.1134 | 0.00019003 | 36706.1134 | 0.001506
4.8138 | 0.0001229 | 4.8138 | 0.0001229 | 4.8138 | 0.0024253 | 4.7119 | 0.00011343 | 4.7119 | 0.0015861 | 4.7119 | 0.002391 | 50383.6216 | 0.0028176 | 50383.6216 | 0.00014453 | 50383.6216 | 0.0011484 | 36706.2735 | 0.0036742 | 36706.2735 | 0.00019002 | 36706.2735 | 0.001506
4.8462 | 0.00012471 | 4.8462 | 0.00012471 | 4.8462 | 0.0024359 | 4.7777 | 0.00011688 | 4.7777 | 0.0015909 | 4.7777 | 0.0024133 | 50421.7018 | 0.0028103 | 50421.7018 | 0.00014375 | 50421.7018 | 0.0011428 | 36706.5674 | 0.0036742 | 36706.5674 | 0.00019001 | 36706.5674 | 0.001506
4.899 | 0.00012764 | 4.899 | 0.00012764 | 4.899 | 0.0024528 | 4.8048 | 0.00011829 | 4.8048 | 0.0015928 | 4.8048 | 0.0024223 | 50459.782 | 0.0028005 | 50459.782 | 0.00014264 | 50459.782 | 0.0011346 | 36707.199 | 0.0036744 | 36707.199 | 0.00018999 | 36707.199 | 0.0015061
4.9518 | 0.0001304 | 4.9518 | 0.0001304 | 4.9518 | 0.0024695 | 4.8186 | 0.00011899 | 4.8186 | 0.0015938 | 4.8186 | 0.0024268 | 50503.2747 | 0.0027861 | 50503.2747 | 0.00014144 | 50503.2747 | 0.0011252 | 36708.2014 | 0.0036747 | 36708.2014 | 0.00018997 | 36708.2014 | 0.0015062
5.0252 | 0.00013422 | 5.0252 | 0.00013422 | 5.0252 | 0.002492 | 4.8514 | 0.00012074 | 4.8514 | 0.001596 | 4.8514 | 0.0024376 | 50546.7673 | 0.002769 | 50546.7673 | 0.00014024 | 50546.7673 | 0.0011158 | 36709.2037 | 0.0036749 | 36709.2037 | 0.00018995 | 36709.2037 | 0.0015063
5.0985 | 0.00013797 | 5.0985 | 0.00013797 | 5.0985 | 0.0025139 | 4.9063 | 0.0001236 | 4.9063 | 0.0015997 | 4.9063 | 0.0024552 | 50603.5282 | 0.0027436 | 50603.5282 | 0.00013867 | 50603.5282 | 0.0011035 | 36710.6737 | 0.0036753 | 36710.6737 | 0.00018993 | 36710.6737 | 0.0015064
5.1488 | 0.0001405 | 5.1488 | 0.0001405 | 5.1488 | 0.0025285 | 4.9611 | 0.00012631 | 4.9611 | 0.0016033 | 4.9611 | 0.0024724 | 50714.8943 | 0.0026875 | 50714.8943 | 0.00013557 | 50714.8943 | 0.0010793 | 36713.9307 | 0.0036762 | 36713.9307 | 0.00018992 | 36713.9307 | 0.0015068
5.157 | 0.00014091 | 5.157 | 0.00014091 | 5.157 | 0.0025309 | 5.041 | 0.00013023 | 5.041 | 0.0016082 | 5.041 | 0.0024968 | 50861.1527 | 0.002606 | 50861.1527 | 0.0001315 | 50861.1527 | 0.0010473 | 36726.1098 | 0.0036796 | 36726.1098 | 0.00019 | 36726.1098 | 0.0015082
5.1599 | 0.00014114 | 5.1599 | 0.00014114 | 5.1599 | 0.0025317 | 5.1407 | 0.00013502 | 5.1407 | 0.0016142 | 5.1407 | 0.0025262 | 51023.8034 | 0.0025095 | 51023.8034 | 0.00012696 | 51023.8034 | 0.0010116 | 36742.4758 | 0.0036845 | 36742.4758 | 0.00019025 | 36742.4758 | 0.0015101
5.1618 | 0.00014168 | 5.1618 | 0.00014168 | 5.1618 | 0.002532 | 5.228 | 0.0001391 | 5.228 | 0.0016191 | 5.228 | 0.002551 | 51152.8069 | 0.0024306 | 51152.8069 | 0.00012336 | 51152.8069 | 0.00098315 | 36758.8417 | 0.0036897 | 36758.8417 | 0.0001905 | 36758.8417 | 0.0015119
5.1634 | 0.00014249 | 5.1634 | 0.00014249 | 5.1634 | 0.0025323 | 5.2415 | 0.00013973 | 5.2415 | 0.0016198 | 5.2415 | 0.0025548 | 51291.7484 | 0.0023445 | 51291.7484 | 0.00011947 | 51291.7484 | 0.00095246 | 36782.2402 | 0.0036976 | 36782.2402 | 0.00019084 | 36782.2402 | 0.0015146
5.165 | 0.00014345 | 5.165 | 0.00014345 | 5.165 | 0.0025326 | 5.2462 | 0.00013997 | 5.2462 | 0.0016201 | 5.2462 | 0.0025561 | 51403.8402 | 0.0022746 | 51403.8402 | 0.00011633 | 51403.8402 | 0.00092766 | 36829.7695 | 0.0037148 | 36829.7695 | 0.00019152 | 36829.7695 | 0.00152
5.1665 | 0.0001444 | 5.1665 | 0.0001444 | 5.1665 | 0.002533 | 5.2486 | 0.00014045 | 5.2486 | 0.0016202 | 5.2486 | 0.0025566 | 51660.2528 | 0.0021138 | 51660.2528 | 0.00010915 | 51660.2528 | 0.00087077 | 36898.162 | 0.0037406 | 36898.162 | 0.0001925 | 36898.162 | 0.0015278
5.1687 | 0.00014555 | 5.1687 | 0.00014555 | 5.1687 | 0.0025336 | 5.2509 | 0.00014151 | 5.2509 | 0.0016203 | 5.2509 | 0.0025569 | 51806.8971 | 0.0020211 | 51806.8971 | 0.00010503 | 51806.8971 | 0.00083812 | 36966.5545 | 0.0037667 | 36966.5545 | 0.00019348 | 36966.5545 | 0.0015356
5.1709 | 0.00014647 | 5.1709 | 0.00014647 | 5.1709 | 0.0025343 | 5.2527 | 0.00014247 | 5.2527 | 0.0016204 | 5.2527 | 0.0025573 | 51941.422 | 0.0019356 | 51941.422 | 0.00010124 | 51941.422 | 0.00080812 | 37034.9471 | 0.0037922 | 37034.9471 | 0.00019446 | 37034.9471 | 0.0015434
5.1734 | 0.00014728 | 5.1734 | 0.00014728 | 5.1734 | 0.002535 | 5.2544 | 0.00014338 | 5.2544 | 0.0016205 | 5.2544 | 0.0025578 | 52156.9058 | 0.0017992 | 52156.9058 | 9.517e-05 | 52156.9058 | 0.00075994 | 37110.3162 | 0.0038194 | 37110.3162 | 0.00019554 | 37110.3162 | 0.0015519
5.1774 | 0.00014823 | 5.1774 | 0.00014823 | 5.1774 | 0.0025361 | 5.2566 | 0.00014436 | 5.2566 | 0.0016206 | 5.2566 | 0.0025584 | 52563.613 | 0.0015468 | 52563.613 | 8.3668e-05 | 52563.613 | 0.00066862 | 37201.7114 | 0.0038512 | 37201.7114 | 0.00019685 | 37201.7114 | 0.0015623
5.1831 | 0.0001491 | 5.1831 | 0.0001491 | 5.1831 | 0.0025378 | 5.2588 | 0.00014513 | 5.2588 | 0.0016207 | 5.2588 | 0.002559 | 52858.9987 | 0.0013675 | 52858.9987 | 7.5269e-05 | 52858.9987 | 0.00060188 | 37316.7919 | 0.0038899 | 37316.7919 | 0.00019849 | 37316.7919 | 0.0015754
5.1889 | 0.00014959 | 5.1889 | 0.00014959 | 5.1889 | 0.0025394 | 5.2616 | 0.0001459 | 5.2616 | 0.0016209 | 5.2616 | 0.0025598 | 53092.3826 | 0.0012296 | 53092.3826 | 6.8602e-05 | 53092.3826 | 0.00054886 | 37462.4061 | 0.0039372 | 37462.4061 | 0.00020057 | 37462.4061 | 0.0015918
5.1958 | 0.00014995 | 5.1958 | 0.00014995 | 5.1958 | 0.0025413 | 5.2674 | 0.00014694 | 5.2674 | 0.0016212 | 5.2674 | 0.0025614 | 53362.4874 | 0.0010756 | 53362.4874 | 6.0846e-05 | 53362.4874 | 0.00048712 | 37649.8936 | 0.0039968 | 37649.8936 | 0.00020323 | 37649.8936 | 0.001613
5.2044 | 0.00015025 | 5.2044 | 0.00015025 | 5.2044 | 0.0025438 | 5.2731 | 0.00014752 | 5.2731 | 0.0016215 | 5.2731 | 0.0025629 | 53739.7234 | 0.00086859 | 53739.7234 | 4.9913e-05 | 53739.7234 | 0.00039997 | 37904.3292 | 0.0040764 | 37904.3292 | 0.00020684 | 37904.3292 | 0.0016416
5.2156 | 0.00015056 | 5.2156 | 0.00015056 | 5.2156 | 0.0025469 | 5.2788 | 0.00014787 | 5.2788 | 0.0016218 | 5.2788 | 0.0025645 | 53848.6019 | 0.0008105 | 53848.6019 | 4.6731e-05 | 53848.6019 | 0.00037457 | 38274.028 | 0.0041906 | 38274.028 | 0.00021206 | 38274.028 | 0.0016831
5.231 | 0.00015095 | 5.231 | 0.00015095 | 5.231 | 0.0025512 | 5.2863 | 0.00014816 | 5.2863 | 0.0016222 | 5.2863 | 0.0025665 | 53939.5602 | 0.00076249 | 53939.5602 | 4.4063e-05 | 53939.5602 | 0.00035326 | 38874.4466 | 0.0043734 | 38874.4466 | 0.00022049 | 38874.4466 | 0.0017499
5.2536 | 0.00015149 | 5.2536 | 0.00015149 | 5.2536 | 0.0025575 | 5.2964 | 0.00014845 | 5.2964 | 0.0016227 | 5.2964 | 0.0025693 | 54000.1343 | 0.0007308 | 54000.1343 | 4.2284e-05 | 54000.1343 | 0.00033904 | 39272.4128 | 0.0044928 | 39272.4128 | 0.00022604 | 39272.4128 | 0.001794
5.29 | 0.00015237 | 5.29 | 0.00015237 | 5.29 | 0.0025675 | 5.3101 | 0.00014878 | 5.3101 | 0.0016235 | 5.3101 | 0.002573 | 54004.8265 | 0.00072838 | 54004.8265 | 4.2272e-05 | 54004.8265 | 0.00033894 | 39597.5437 | 0.0045894 | 39597.5437 | 0.00023055 | 39597.5437 | 0.0018298
5.3568 | 0.00015398 | 5.3568 | 0.00015398 | 5.3568 | 0.0025855 | 5.329 | 0.0001492 | 5.329 | 0.0016245 | 5.329 | 0.0025781 | 54009.5188 | 0.00072603 | 54009.5188 | 4.2294e-05 | 54009.5188 | 0.0003389 | 39633.1584 | 0.0045982 | 39633.1584 | 0.00023048 | 39633.1584 | 0.0018293
5.49 | 0.00015715 | 5.49 | 0.00015715 | 5.49 | 0.0026199 | 5.3574 | 0.00014983 | 5.3574 | 0.001626 | 5.3574 | 0.0025857 | 54014.211 | 0.00072375 | 54014.211 | 4.2308e-05 | 54014.211 | 0.00033883 | 39668.773 | 0.0046047 | 39668.773 | 0.00023035 | 39668.773 | 0.0018283
5.5831 | 0.00015932 | 5.5831 | 0.00015932 | 5.5831 | 0.0026429 | 5.4058 | 0.0001509 | 5.4058 | 0.0016285 | 5.4058 | 0.0025984 | 54023.4712 | 0.00071945 | 54023.4712 | 4.2314e-05 | 54023.4712 | 0.00033868 | 39704.3876 | 0.0046088 | 39704.3876 | 0.00023023 | 39704.3876 | 0.0018273
5.5982 | 0.00015967 | 5.5982 | 0.00015967 | 5.5982 | 0.0026466 | 5.5043 | 0.00015306 | 5.5043 | 0.0016335 | 5.5043 | 0.0026235 | 54042.2113 | 0.0007115 | 54042.2113 | 4.2297e-05 | 54042.2113 | 0.00033839 | 39768.5117 | 0.0046121 | 39768.5117 | 0.00023001 | 39768.5117 | 0.0018256
5.6032 | 0.00015973 | 5.6032 | 0.00015973 | 5.6032 | 0.0026478 | 5.6421 | 0.00015603 | 5.6421 | 0.0016401 | 5.6421 | 0.0026571 | 54074.1281 | 0.00069995 | 54074.1281 | 4.2249e-05 | 54074.1281 | 0.0003379 | 39870.0804 | 0.0046102 | 39870.0804 | 0.00022966 | 39870.0804 | 0.0018228
5.6141 | 0.00015992 | 5.6141 | 0.00015992 | 5.6141 | 0.0026504 | 5.6685 | 0.00015658 | 5.6685 | 0.0016414 | 5.6685 | 0.0026633 | 54126.0216 | 0.00068544 | 54126.0216 | 4.2171e-05 | 54126.0216 | 0.0003371 | 39981.2737 | 0.0046021 | 39981.2737 | 0.00022928 | 39981.2737 | 0.0018198
5.6282 | 0.00016034 | 5.6282 | 0.00016034 | 5.6282 | 0.0026537 | 5.6726 | 0.00015662 | 5.6726 | 0.0016416 | 5.6726 | 0.0026642 | 54217.3733 | 0.00066861 | 54217.3733 | 4.2035e-05 | 54217.3733 | 0.0003357 | 40101.3131 | 0.0045905 | 40101.3131 | 0.00022887 | 40101.3131 | 0.0018165
5.6477 | 0.00016083 | 5.6477 | 0.00016083 | 5.6477 | 0.0026584 | 5.6817 | 0.00015676 | 5.6817 | 0.001642 | 5.6817 | 0.0026664 | 54388.0185 | 0.0006528 | 54388.0185 | 4.1771e-05 | 54388.0185 | 0.00033314 | 40249.1713 | 0.004575 | 40249.1713 | 0.00022836 | 40249.1713 | 0.0018125
5.6672 | 0.00016127 | 5.6672 | 0.00016127 | 5.6672 | 0.002663 | 5.6936 | 0.00015708 | 5.6936 | 0.0016425 | 5.6936 | 0.0026691 | 54602.7864 | 0.00064614 | 54602.7864 | 4.1423e-05 | 54602.7864 | 0.00032994 | 40449.2085 | 0.0045542 | 40449.2085 | 0.00022767 | 40449.2085 | 0.001807
5.7034 | 0.00016208 | 5.7034 | 0.00016208 | 5.7034 | 0.0026714 | 5.7119 | 0.00015752 | 5.7119 | 0.0016434 | 5.7119 | 0.0026734 | 54817.5542 | 0.00064374 | 54817.5542 | 4.106e-05 | 54817.5542 | 0.00032676 | 40734.6928 | 0.0045262 | 40734.6928 | 0.00022669 | 40734.6928 | 0.0017992
5.7596 | 0.00016335 | 5.7596 | 0.00016335 | 5.7596 | 0.0026842 | 5.7335 | 0.00015797 | 5.7335 | 0.0016444 | 5.7335 | 0.0026783 | 55032.3221 | 0.00064129 | 55032.3221 | 4.0688e-05 | 55032.3221 | 0.00032359 | 41174.283 | 0.0044864 | 41174.283 | 0.00022518 | 41174.283 | 0.0017872
5.8706 | 0.00016584 | 5.8706 | 0.00016584 | 5.8706 | 0.0027088 | 5.7721 | 0.00015877 | 5.7721 | 0.0016461 | 5.7721 | 0.002687 | 55252.781 | 0.00063814 | 55252.781 | 4.0298e-05 | 55252.781 | 0.00032034 | 42117.816 | 0.0044085 | 42117.816 | 0.00022193 | 42117.816 | 0.0017614
6.151 | 0.00017193 | 6.151 | 0.00017193 | 6.151 | 0.0027662 | 5.8308 | 0.00015998 | 5.8308 | 0.0016486 | 5.8308 | 0.0027001 | 55497.0972 | 0.00063414 | 55497.0972 | 3.986e-05 | 55497.0972 | 0.00031675 | 43162.5214 | 0.0043283 | 43162.5214 | 0.00021832 | 43162.5214 | 0.0017327
6.5474 | 0.0001801 | 6.5474 | 0.0001801 | 6.5474 | 0.0028372 | 5.934 | 0.0001621 | 5.934 | 0.001653 | 5.934 | 0.0027223 | 55777.8616 | 0.00062902 | 55777.8616 | 3.9351e-05 | 55777.8616 | 0.00031262 | 43230.6574 | 0.0043204 | 43230.6574 | 0.00021753 | 43230.6574 | 0.0017265
6.9751 | 0.00018837 | 6.9751 | 0.00018837 | 6.9751 | 0.0029022 | 6.2424 | 0.00016821 | 6.2424 | 0.0016647 | 6.2424 | 0.0027835 | 56101.2813 | 0.00062239 | 56101.2813 | 3.876e-05 | 56101.2813 | 0.00030786 | 43298.7933 | 0.0043053 | 43298.7933 | 0.00021606 | 43298.7933 | 0.0017149
7.4684 | 0.00019722 | 7.4684 | 0.00019722 | 7.4684 | 0.0029646 | 6.6476 | 0.00017579 | 6.6476 | 0.0016775 | 6.6476 | 0.0028534 | 56473.1286 | 0.00061387 | 56473.1286 | 3.8075e-05 | 56473.1286 | 0.00030239 | 43359.2476 | 0.004286 | 43359.2476 | 0.00021474 | 43359.2476 | 0.0017045
8.1798 | 0.00020878 | 8.1798 | 0.00020878 | 8.1798 | 0.0030358 | 7.0527 | 0.00018286 | 7.0527 | 0.0016877 | 7.0527 | 0.0029128 | 56905.639 | 0.00060309 | 56905.639 | 3.7276e-05 | 56905.639 | 0.00029601 | 43419.7019 | 0.0042624 | 43419.7019 | 0.00021344 | 43419.7019 | 0.0016941
9.0532 | 0.00022118 | 9.0532 | 0.00022118 | 9.0532 | 0.0030997 | 7.5317 | 0.0001906 | 7.5317 | 0.0016971 | 7.5317 | 0.0029717 | 57424.0954 | 0.00058935 | 57424.0954 | 3.6313e-05 | 57424.0954 | 0.00028836 | 43505.932 | 0.0042243 | 43505.932 | 0.00021156 | 43505.932 | 0.0016793
9.9953 | 0.0002326 | 9.9953 | 0.0002326 | 9.9953 | 0.0031474 | 8.2439 | 0.00020094 | 8.2439 | 0.001707 | 8.2439 | 0.0030412 | 57625.961 | 0.00058349 | 57625.961 | 3.5896e-05 | 57625.961 | 0.00028505 | 43620.3696 | 0.0041693 | 43620.3696 | 0.00020907 | 43620.3696 | 0.0016595
10.9374 | 0.00024224 | 10.9374 | 0.00024224 | 10.9374 | 0.0031798 | 9.13 | 0.00021201 | 9.13 | 0.0017143 | 9.13 | 0.0031043 | 57706.363 | 0.0005806 | 57706.363 | 3.5616e-05 | 57706.363 | 0.00028286 | 43758.2934 | 0.0040999 | 43758.2934 | 0.00020607 | 43758.2934 | 0.0016356
12.0249 | 0.00025169 | 12.0249 | 0.00025169 | 12.0249 | 0.0032046 | 10.084 | 0.00022199 | 10.084 | 0.0017182 | 10.084 | 0.003151 | 57773.1553 | 0.00057775 | 57773.1553 | 3.5386e-05 | 57773.1553 | 0.00028104 | 43928.1313 | 0.0040128 | 43928.1313 | 0.00020235 | 43928.1313 | 0.0016061
13.2828 | 0.00026117 | 13.2828 | 0.00026117 | 13.2828 | 0.0032225 | 11.1078 | 0.00023085 | 11.1078 | 0.0017197 | 11.1078 | 0.0031845 | 57839.9476 | 0.00057461 | 57839.9476 | 3.5157e-05 | 57839.9476 | 0.00027922 | 44151.2647 | 0.0038981 | 44151.2647 | 0.00019745 | 44151.2647 | 0.0015672
14.5484 | 0.00026957 | 14.5484 | 0.00026957 | 14.5484 | 0.0032331 | 12.1315 | 0.00023817 | 12.1315 | 0.0017196 | 12.1315 | 0.0032065 | 57974.4311 | 0.00056782 | 57974.4311 | 3.4693e-05 | 57974.4311 | 0.00027555 | 44469.2309 | 0.0037349 | 44469.2309 | 0.00019043 | 44469.2309 | 0.0015115
15.899 | 0.00027775 | 15.899 | 0.00027775 | 15.899 | 0.0032396 | 13.2888 | 0.00024505 | 13.2888 | 0.0017184 | 13.2888 | 0.0032224 | 58484.4277 | 0.00054057 | 58484.4277 | 3.2933e-05 | 58484.4277 | 0.00026159 | 44699.8719 | 0.0036164 | 44699.8719 | 0.0001853 | 44699.8719 | 0.0014708
17.427 | 0.00028645 | 17.427 | 0.00028645 | 17.427 | 0.0032437 | 14.446 | 0.000251 | 14.446 | 0.0017167 | 14.446 | 0.0032322 | 59263.6963 | 0.0004976 | 59263.6963 | 3.0233e-05 | 59263.6963 | 0.00024014 | 44761.9861 | 0.0035845 | 44761.9861 | 0.00018392 | 44761.9861 | 0.0014598
18.9549 | 0.00029481 | 18.9549 | 0.00029481 | 18.9549 | 0.0032458 | 15.7681 | 0.00025704 | 15.7681 | 0.0017144 | 15.7681 | 0.003239 | 60060.1643 | 0.00045348 | 60060.1643 | 2.7456e-05 | 60060.1643 | 0.00021807 | 44772.0375 | 0.0035794 | 44772.0375 | 0.0001837 | 44772.0375 | 0.001458
20.9677 | 0.00030564 | 20.9677 | 0.00030564 | 20.9677 | 0.0032472 | 17.0902 | 0.00026256 | 17.0902 | 0.0017119 | 17.0902 | 0.0032429 | 60902.0855 | 0.00040639 | 60902.0855 | 2.4499e-05 | 60902.0855 | 0.00019455 | 44777.5207 | 0.0035765 | 44777.5207 | 0.00018357 | 44777.5207 | 0.0014571
23.5799 | 0.00031963 | 23.5799 | 0.00031963 | 23.5799 | 0.0032479 | 18.786 | 0.00026921 | 18.786 | 0.0017087 | 18.786 | 0.0032457 | 61167.2429 | 0.00039137 | 61167.2429 | 2.3562e-05 | 61167.2429 | 0.0001871 | 44784.0001 | 0.0035732 | 44784.0001 | 0.00018338 | 44784.0001 | 0.0014559
26.8713 | 0.00033739 | 26.8713 | 0.00033739 | 26.8713 | 0.0032482 | 20.8928 | 0.00027712 | 20.8928 | 0.0017046 | 20.8928 | 0.0032472 | 61217.9156 | 0.00038868 | 61217.9156 | 2.3448e-05 | 61217.9156 | 0.00018618 | 44790.4795 | 0.0035699 | 44790.4795 | 0.00018318 | 44790.4795 | 0.0014547
29.6676 | 0.00035269 | 29.6676 | 0.00035269 | 29.6676 | 0.0032482 | 22.9996 | 0.00028484 | 22.9996 | 0.0017006 | 22.9996 | 0.0032478 | 61268.5883 | 0.0003866 | 61268.5883 | 2.3452e-05 | 61268.5883 | 0.0001862 | 44806.4107 | 0.0035619 | 44806.4107 | 0.00018278 | 44806.4107 | 0.0014518
30.0763 | 0.00035494 | 30.0763 | 0.00035494 | 30.0763 | 0.0032482 | 25.875 | 0.00029531 | 25.875 | 0.001695 | 25.875 | 0.0032481 | 61304.1928 | 0.00038556 | 61304.1928 | 2.3454e-05 | 61304.1928 | 0.00018621 | 44871.117 | 0.0035317 | 44871.117 | 0.00018126 | 44871.117 | 0.0014401
30.1541 | 0.00035537 | 30.1541 | 0.00035537 | 30.1541 | 0.0032482 | 29.8948 | 0.00030996 | 29.8948 | 0.0016873 | 29.8948 | 0.0032482 | 61339.7973 | 0.00038481 | 61339.7973 | 2.3456e-05 | 61339.7973 | 0.00018622 | 44926.2032 | 0.0035069 | 44926.2032 | 0.00017998 | 44926.2032 | 0.0014301
30.1726 | 0.00035547 | 30.1726 | 0.00035547 | 30.1726 | 0.0032482 | 35.6007 | 0.0003309 | 35.6007 | 0.0016764 | 35.6007 | 0.0032482 | 61393.2759 | 0.00038409 | 61393.2759 | 2.3459e-05 | 61393.2759 | 0.00018624 | 44981.2894 | 0.0034829 | 44981.2894 | 0.00017868 | 44981.2894 | 0.00142
30.177 | 0.0003555 | 30.177 | 0.0003555 | 30.177 | 0.0032482 | 44.5042 | 0.00036392 | 44.5042 | 0.0016593 | 44.5042 | 0.0032482 | 61688.6682 | 0.00038327 | 61688.6682 | 2.3474e-05 | 61688.6682 | 0.00018633 | 45102.0847 | 0.003432 | 45102.0847 | 0.00017584 | 45102.0847 | 0.0013979
30.1785 | 0.00035551 | 30.1785 | 0.00035551 | 30.1785 | 0.0032482 | 56.3948 | 0.00040836 | 56.3948 | 0.0016366 | 56.3948 | 0.0032482 | 62249.1968 | 0.0003859 | 62249.1968 | 2.35e-05 | 62249.1968 | 0.00018652 | 45210.1316 | 0.0033879 | 45210.1316 | 0.0001733 | 45210.1316 | 0.001378
30.1787 | 0.00035551 | 30.1787 | 0.00035551 | 30.1787 | 0.0032482 | 59.8133 | 0.00042098 | 59.8133 | 0.0016304 | 59.8133 | 0.0032482 | 62940.8739 | 0.00038884 | 62940.8739 | 2.3529e-05 | 62940.8739 | 0.00018674 | 45307.8832 | 0.0033483 | 45307.8832 | 0.000171 | 45307.8832 | 0.00136
30.1787 | 0.00035551 | 30.1787 | 0.00035551 | 30.1787 | 0.0032482 | 62.7106 | 0.00043154 | 62.7106 | 0.0016251 | 62.7106 | 0.0032482 | 63748.1398 | 0.00039019 | 63748.1398 | 2.3562e-05 | 63748.1398 | 0.000187 | 45397.1063 | 0.003312 | 45397.1063 | 0.00016889 | 45397.1063 | 0.0013435
30.1787 | 0.00035551 | 30.1787 | 0.00035551 | 30.1787 | 0.0032482 | 63.7242 | 0.00043523 | 63.7242 | 0.0016233 | 63.7242 | 0.0032482 | 64716.4796 | 0.00039092 | 64716.4796 | 2.3602e-05 | 64716.4796 | 0.00018732 | 45486.3628 | 0.0032755 | 45486.3628 | 0.00016679 | 45486.3628 | 0.0013269
30.1787 | 0.00035551 | 30.1787 | 0.00035551 | 30.1787 | 0.0032482 | 63.879 | 0.00043579 | 63.879 | 0.001623 | 63.879 | 0.0032482 | 65420.699 | 0.0003905 | 65420.699 | 2.3565e-05 | 65420.699 | 0.00018703 | 45582.2279 | 0.0032358 | 45582.2279 | 0.00016453 | 45582.2279 | 0.0013091
30.1787 | 0.00035551 | 30.1787 | 0.00035551 | 30.1787 | 0.0032482 | 63.8976 | 0.00043586 | 63.8976 | 0.0016229 | 63.8976 | 0.0032482 | 66124.9183 | 0.00038972 | 66124.9183 | 2.352e-05 | 66124.9183 | 0.00018667 | 45687.2493 | 0.0031916 | 45687.2493 | 0.00016205 | 45687.2493 | 0.0012895
30.1787 | 0.00035551 | 30.1787 | 0.00035551 | 30.1787 | 0.0032482 | 63.9023 | 0.00043588 | 63.9023 | 0.0016229 | 63.9023 | 0.0032482 | 66829.1377 | 0.00038894 | 66829.1377 | 2.3475e-05 | 66829.1377 | 0.00018631 | 45768.6451 | 0.0031569 | 45768.6451 | 0.00016013 | 45768.6451 | 0.0012744
30.1787 | 0.00035551 | 30.1787 | 0.00035551 | 30.1787 | 0.0032482 | 63.9034 | 0.00043588 | 63.9034 | 0.0016229 | 63.9034 | 0.0032482 | 68001.0336 | 0.00038773 | 68001.0336 | 2.34e-05 | 68001.0336 | 0.00018572 | 45882.9478 | 0.0031074 | 45882.9478 | 0.00015743 | 45882.9478 | 0.001253
30.1787 | 0.00035551 | 30.1787 | 0.00035551 | 30.1787 | 0.0032482 | 63.9038 | 0.00043588 | 63.9038 | 0.0016229 | 63.9038 | 0.0032482 | 69729.0336 | 0.00038643 | 69729.0336 | 2.3321e-05 | 69729.0336 | 0.00018509 | 46073.5741 | 0.003023 | 46073.5741 | 0.00015292 | 46073.5741 | 0.0012174
30.1788 | 0.00035551 | 30.1788 | 0.00035551 | 30.1788 | 0.0032482 | 63.9038 | 0.00043588 | 63.9038 | 0.0016229 | 63.9038 | 0.0032482 | 71457.0336 | 0.00038534 | 71457.0336 | 2.3251e-05 | 71457.0336 | 0.00018453 | 46158.8749 | 0.0029844 | 46158.8749 | 0.0001509 | 46158.8749 | 0.0012014
30.1788 | 0.00035551 | 30.1788 | 0.00035551 | 30.1788 | 0.0032482 | 63.9038 | 0.00043588 | 63.9038 | 0.0016229 | 63.9038 | 0.0032482 | 72613.7989 | 0.00038567 | 72613.7989 | 2.3279e-05 | 72613.7989 | 0.00018475 | 46240.548 | 0.0029468 | 46240.548 | 0.00014896 | 46240.548 | 0.0011861
30.1788 | 0.00035551 | 30.1788 | 0.00035551 | 30.1788 | 0.0032482 | 63.9038 | 0.00043588 | 63.9038 | 0.0016229 | 63.9038 | 0.0032482 | 73770.5642 | 0.00038717 | 73770.5642 | 2.3373e-05 | 73770.5642 | 0.0001855 | 46365.0191 | 0.0028884 | 46365.0191 | 0.00014601 | 46365.0191 | 0.0011628
30.1788 | 0.00035551 | 30.1788 | 0.00035551 | 30.1788 | 0.0032482 | 63.9038 | 0.00043588 | 63.9038 | 0.0016229 | 63.9038 | 0.0032482 | 74970.1206 | 0.00038884 | 74970.1206 | 2.347e-05 | 74970.1206 | 0.00018627 | 46478.0811 | 0.0028343 | 46478.0811 | 0.00014333 | 46478.0811 | 0.0011415
30.1788 | 0.00035551 | 30.1788 | 0.00035551 | 30.1788 | 0.0032482 | 63.9038 | 0.00043588 | 63.9038 | 0.0016229 | 63.9038 | 0.0032482 | 75829.2701 | 0.00038936 | 75829.2701 | 2.3496e-05 | 75829.2701 | 0.00018648 | 46592.3099 | 0.0027787 | 46592.3099 | 0.00014063 | 46592.3099 | 0.0011201
30.1788 | 0.00035551 | 30.1788 | 0.00035551 | 30.1788 | 0.0032482 | 63.9038 | 0.00043588 | 63.9038 | 0.0016229 | 63.9038 | 0.0032482 | 76523.4676 | 0.00038834 | 76523.4676 | 2.3419e-05 | 76523.4676 | 0.00018587 | 46707.8678 | 0.0027216 | 46707.8678 | 0.00013789 | 46707.8678 | 0.0010983
30.1789 | 0.00035551 | 30.1789 | 0.00035551 | 30.1789 | 0.0032482 | 63.9038 | 0.00043588 | 63.9038 | 0.0016229 | 63.9038 | 0.0032482 | 77046.3805 | 0.00038725 | 77046.3805 | 2.3362e-05 | 77046.3805 | 0.00018541 | 46807.2023 | 0.002674 | 46807.2023 | 0.00013592 | 46807.2023 | 0.0010824
30.179 | 0.00035551 | 30.179 | 0.00035551 | 30.179 | 0.0032482 | 63.9039 | 0.00043588 | 63.9039 | 0.0016229 | 63.9039 | 0.0032482 | 77569.2934 | 0.00038624 | 77569.2934 | 2.3304e-05 | 77569.2934 | 0.00018496 | 46815.3695 | 0.0026704 | 46815.3695 | 0.00013619 | 46815.3695 | 0.001084
30.1792 | 0.00035551 | 30.1792 | 0.00035551 | 30.1792 | 0.0032482 | 63.9039 | 0.00043588 | 63.9039 | 0.0016229 | 63.9039 | 0.0032482 | 78441.2046 | 0.00038467 | 78441.2046 | 2.3208e-05 | 78441.2046 | 0.00018419 | 46821.9156 | 0.0026678 | 46821.9156 | 0.00013647 | 46821.9156 | 0.0010854
30.1795 | 0.00035551 | 30.1795 | 0.00035551 | 30.1795 | 0.0032482 | 63.9039 | 0.00043588 | 63.9039 | 0.0016229 | 63.9039 | 0.0032482 | 79595.177 | 0.00038341 | 79595.177 | 2.3136e-05 | 79595.177 | 0.00018362 | 46828.4616 | 0.0026654 | 46828.4616 | 0.00013668 | 46828.4616 | 0.0010867
30.1798 | 0.00035551 | 30.1798 | 0.00035551 | 30.1798 | 0.0032482 | 63.9039 | 0.00043588 | 63.9039 | 0.0016229 | 63.9039 | 0.0032482 | 80749.1494 | 0.00038386 | 80749.1494 | 2.3169e-05 | 80749.1494 | 0.00018389 | 46835.0077 | 0.0026634 | 46835.0077 | 0.00013687 | 46835.0077 | 0.001088
30.1801 | 0.00035552 | 30.1801 | 0.00035552 | 30.1801 | 0.0032482 | 63.9039 | 0.00043588 | 63.9039 | 0.001623 | 63.9039 | 0.0032482 | 81585.8514 | 0.0003844 | 81585.8514 | 2.3194e-05 | 81585.8514 | 0.00018408 | 46847.506 | 0.0026601 | 46847.506 | 0.0001372 | 46847.506 | 0.0010905
30.1805 | 0.00035552 | 30.1805 | 0.00035552 | 30.1805 | 0.0032482 | 63.9039 | 0.00043588 | 63.9039 | 0.001623 | 63.9039 | 0.0032482 | 82422.5535 | 0.00038481 | 82422.5535 | 2.3218e-05 | 82422.5535 | 0.00018427 | 46874.913 | 0.0026554 | 46874.913 | 0.00013793 | 46874.913 | 0.0010959
30.1808 | 0.00035552 | 30.1808 | 0.00035552 | 30.1808 | 0.0032482 | 63.904 | 0.00043588 | 63.904 | 0.001623 | 63.904 | 0.0032482 | 83735.5144 | 0.00038542 | 83735.5144 | 2.3256e-05 | 83735.5144 | 0.00018457 | 46921.0498 | 0.0026542 | 46921.0498 | 0.00013916 | 46921.0498 | 0.0011052
30.1813 | 0.00035552 | 30.1813 | 0.00035552 | 30.1813 | 0.0032482 | 63.9041 | 0.00043588 | 63.9041 | 0.001623 | 63.9041 | 0.0032482 | 85463.5144 | 0.00038622 | 85463.5144 | 2.3306e-05 | 85463.5144 | 0.00018497 | 46986.0915 | 0.0026632 | 46986.0915 | 0.00014088 | 46986.0915 | 0.0011183
30.182 | 0.00035553 | 30.182 | 0.00035553 | 30.182 | 0.0032482 | 63.9043 | 0.00043588 | 63.9043 | 0.0016231 | 63.9043 | 0.0032482 | 86400 | 0.00038665 | 86400 | 2.3333e-05 | 86400 | 0.00018519 | 47053.7509 | 0.0026822 | 47053.7509 | 0.00014268 | 47053.7509 | 0.001132
30.1828 | 0.00035553 | 30.1828 | 0.00035553 | 30.1828 | 0.0032482 | 63.9044 | 0.00043588 | 63.9044 | 0.0016231 | 63.9044 | 0.0032482 | [6 empty] | 47126.1493 | 0.0027097 | 47126.1493 | 0.0001446 | 47126.1493 | 0.0011467
30.1838 | 0.00035554 | 30.1838 | 0.00035554 | 30.1838 | 0.0032482 | 63.9047 | 0.00043588 | 63.9047 | 0.0016232 | 63.9047 | 0.0032482 | [6 empty] | 47221.2718 | 0.0027525 | 47221.2718 | 0.00014712 | 47221.2718 | 0.0011661
30.1851 | 0.00035554 | 30.1851 | 0.00035554 | 30.1851 | 0.0032482 | 63.905 | 0.00043589 | 63.905 | 0.0016233 | 63.905 | 0.0032482 | [6 empty] | 47356.3624 | 0.0028211 | 47356.3624 | 0.00015069 | 47356.3624 | 0.0011938
30.1867 | 0.00035555 | 30.1867 | 0.00035555 | 30.1867 | 0.0032482 | 63.9053 | 0.00043589 | 63.9053 | 0.0016234 | 63.9053 | 0.0032482 | [6 empty] | 47536.3786 | 0.0029204 | 47536.3786 | 0.00015545 | 47536.3786 | 0.0012308
30.1887 | 0.00035556 | 30.1887 | 0.00035556 | 30.1887 | 0.0032482 | 63.9057 | 0.00043589 | 63.9057 | 0.0016235 | 63.9057 | 0.0032482 | [6 empty] | 47659.1852 | 0.0029913 | 47659.1852 | 0.00015869 | 47659.1852 | 0.0012563
30.1912 | 0.00035558 | 30.1912 | 0.00035558 | 30.1912 | 0.0032482 | 63.906 | 0.00043589 | 63.906 | 0.0016236 | 63.906 | 0.0032482 | [6 empty] | 47765.7839 | 0.0030537 | 47765.7839 | 0.00016151 | 47765.7839 | 0.0012784
30.1947 | 0.0003556 | 30.1947 | 0.0003556 | 30.1947 | 0.0032482 | 63.9065 | 0.00043589 | 63.9065 | 0.0016238 | 63.9065 | 0.0032482 | [6 empty] | 47885.5871 | 0.0031242 | 47885.5871 | 0.00016468 | 47885.5871 | 0.0013033
30.1995 | 0.00035562 | 30.1995 | 0.00035562 | 30.1995 | 0.0032482 | 63.9072 | 0.00043589 | 63.9072 | 0.001624 | 63.9072 | 0.0032482 | [6 empty] | 47963.7607 | 0.0031702 | 47963.7607 | 0.00016675 | 47963.7607 | 0.0013196
30.2061 | 0.00035566 | 30.2061 | 0.00035566 | 30.2061 | 0.0032482 | 63.908 | 0.0004359 | 63.908 | 0.0016242 | 63.908 | 0.0032482 | [6 empty] | 48052.3954 | 0.0032223 | 48052.3954 | 0.00016909 | 48052.3954 | 0.0013381
30.2157 | 0.00035571 | 30.2157 | 0.00035571 | 30.2157 | 0.0032482 | 63.9091 | 0.0004359 | 63.9091 | 0.0016245 | 63.9091 | 0.0032482 | [6 empty] | 48123.5982 | 0.0032638 | 48123.5982 | 0.00017097 | 48123.5982 | 0.001353
30.2301 | 0.00035579 | 30.2301 | 0.00035579 | 30.2301 | 0.0032482 | 63.9104 | 0.00043591 | 63.9104 | 0.0016248 | 63.9104 | 0.0032482 | [6 empty] | 48269.9834 | 0.0033477 | 48269.9834 | 0.00017485 | 48269.9834 | 0.0013836
30.2491 | 0.0003559 | 30.2491 | 0.0003559 | 30.2491 | 0.0032482 | 63.912 | 0.00043591 | 63.912 | 0.0016251 | 63.912 | 0.0032482 | [6 empty] | 48346.5648 | 0.0033908 | 48346.5648 | 0.00017687 | 48346.5648 | 0.0013996
30.2722 | 0.00035603 | 30.2722 | 0.00035603 | 30.2722 | 0.0032482 | 63.9139 | 0.00043592 | 63.9139 | 0.0016255 | 63.9139 | 0.0032482 | [6 empty] | 48420.8917 | 0.0034322 | 48420.8917 | 0.00017883 | 48420.8917 | 0.0014152
30.3022 | 0.0003562 | 30.3022 | 0.0003562 | 30.3022 | 0.0032482 | 63.9165 | 0.00043593 | 63.9165 | 0.001626 | 63.9165 | 0.0032482 | [6 empty] | 48511.49 | 0.003482 | 48511.49 | 0.00018123 | 48511.49 | 0.0014341
30.3485 | 0.00035646 | 30.3485 | 0.00035646 | 30.3485 | 0.0032482 | 63.9201 | 0.00043594 | 63.9201 | 0.0016264 | 63.9201 | 0.0032482 | [6 empty] | 48579.4929 | 0.0035189 | 48579.4929 | 0.00018303 | 48579.4929 | 0.0014484
30.4393 | 0.00035697 | 30.4393 | 0.00035697 | 30.4393 | 0.0032482 | 63.9249 | 0.00043596 | 63.9249 | 0.001627 | 63.9249 | 0.0032482 | [6 empty] | 48673.9001 | 0.0035692 | 48673.9001 | 0.00018553 | 48673.9001 | 0.0014682
30.5764 | 0.00035774 | 30.5764 | 0.00035774 | 30.5764 | 0.0032482 | 63.9317 | 0.00043598 | 63.9317 | 0.0016275 | 63.9317 | 0.0032482 | [6 empty] | 48761.7785 | 0.0036152 | 48761.7785 | 0.00018785 | 48761.7785 | 0.0014866
30.9163 | 0.00035965 | 30.9163 | 0.00035965 | 30.9163 | 0.0032482 | 63.9415 | 0.00043602 | 63.9415 | 0.0016279 | 63.9415 | 0.0032482 | [6 empty] | 48821.4495 | 0.0036459 | 48821.4495 | 0.00018944 | 48821.4495 | 0.0014992
31.6345 | 0.00036369 | 31.6345 | 0.00036369 | 31.6345 | 0.0032482 | 63.9562 | 0.00043607 | 63.9562 | 0.0016282 | 63.9562 | 0.0032482 | [6 empty] | 48889.5986 | 0.0036803 | 48889.5986 | 0.00019124 | 48889.5986 | 0.0015135
32.3528 | 0.00036774 | 32.3528 | 0.00036774 | 32.3528 | 0.0032482 | 63.9754 | 0.00043615 | 63.9754 | 0.0016283 | 63.9754 | 0.0032482 | [6 empty] | 48952.0505 | 0.0037113 | 48952.0505 | 0.0001929 | 48952.0505 | 0.0015266
33.0967 | 0.00037195 | 33.0967 | 0.00037195 | 33.0967 | 0.0032482 | 63.9985 | 0.00043623 | 63.9985 | 0.0016283 | 63.9985 | 0.0032482 | [6 empty] | 49007.7315 | 0.0037385 | 49007.7315 | 0.00019437 | 49007.7315 | 0.0015383
34.2099 | 0.00037826 | 34.2099 | 0.00037826 | 34.2099 | 0.0032482 | 64.0284 | 0.00043634 | 64.0284 | 0.0016283 | 64.0284 | 0.0032482 | [6 empty] | 49021.3358 | 0.0037451 | 49021.3358 | 0.00019473 | 49021.3358 | 0.0015412
35.323 | 0.00038461 | 35.323 | 0.00038461 | 35.323 | 0.0032482 | 64.0748 | 0.00043652 | 64.0748 | 0.0016283 | 64.0748 | 0.0032482 | [6 empty] | 49021.4761 | 0.0037451 | 49021.4761 | 0.00019474 | 49021.4761 | 0.0015412
36.4739 | 0.00039121 | 36.4739 | 0.00039121 | 36.4739 | 0.0032482 | 64.1711 | 0.00043688 | 64.1711 | 0.0016282 | 64.1711 | 0.0032482 | [6 empty] | 49021.5662 | 0.0037452 | 49021.5662 | 0.00019474 | 49021.5662 | 0.0015412
37.6686 | 0.0003981 | 37.6686 | 0.0003981 | 37.6686 | 0.0032482 | 64.2921 | 0.00043733 | 64.2921 | 0.0016282 | 64.2921 | 0.0032482 | [6 empty] | 49021.6642 | 0.0037452 | 49021.6642 | 0.00019474 | 49021.6642 | 0.0015412
39.1485 | 0.00040669 | 39.1485 | 0.00040669 | 39.1485 | 0.0032482 | 64.5566 | 0.00043832 | 64.5566 | 0.001628 | 64.5566 | 0.0032482 | [6 empty] | 49021.7272 | 0.0037452 | 49021.7272 | 0.00019474 | 49021.7272 | 0.0015413
41.31 | 0.00041929 | 41.31 | 0.00041929 | 41.31 | 0.0032482 | 64.9532 | 0.00043979 | 64.9532 | 0.0016276 | 64.9532 | 0.0032482 | [6 empty] | 49021.812 | 0.0037453 | 49021.812 | 0.00019474 | 49021.812 | 0.0015413
44.8117 | 0.00043977 | 44.8117 | 0.00043977 | 44.8117 | 0.0032482 | 65.7519 | 0.00044274 | 65.7519 | 0.0016266 | 65.7519 | 0.0032482 | [6 empty] | 49022.0999 | 0.0037454 | 49022.0999 | 0.00019473 | 49022.0999 | 0.0015413
50.8708 | 0.00047592 | 50.8708 | 0.00047592 | 50.8708 | 0.0032482 | 66.3281 | 0.00044485 | 66.3281 | 0.0016258 | 66.3281 | 0.0032482 | [6 empty] | 49022.3126 | 0.0037455 | 49022.3126 | 0.00019471 | 49022.3126 | 0.0015413
58.0408 | 0.00051984 | 58.0408 | 0.00051984 | 58.0408 | 0.0032482 | 66.9043 | 0.00044696 | 66.9043 | 0.001625 | 66.9043 | 0.0032482 | [6 empty] | 49022.5252 | 0.0037456 | 49022.5252 | 0.0001947 | 49022.5252 | 0.0015413
62.7729 | 0.00054925 | 62.7729 | 0.00054925 | 62.7729 | 0.0032482 | 67.7728 | 0.00045013 | 67.7728 | 0.0016239 | 67.7728 | 0.0032482 | [6 empty] | 49022.6893 | 0.0037457 | 49022.6893 | 0.00019469 | 49022.6893 | 0.0015413
67.5051 | 0.00057886 | 67.5051 | 0.00057886 | 67.5051 | 0.0032482 | 68.854 | 0.00045408 | 68.854 | 0.0016225 | 68.854 | 0.0032482 | [6 empty] | 49022.8625 | 0.0037458 | 49022.8625 | 0.00019468 | 49022.8625 | 0.0015413
72.9761 | 0.00061358 | 72.9761 | 0.00061358 | 72.9761 | 0.0032482 | 69.9714 | 0.00045815 | 69.9714 | 0.001621 | 69.9714 | 0.0032482 | [6 empty] | 49023.0824 | 0.0037459 | 49023.0824 | 0.00019466 | 49023.0824 | 0.0015414
79.0058 | 0.00065253 | 79.0058 | 0.00065253 | 79.0058 | 0.0032482 | 71.0888 | 0.00046224 | 71.0888 | 0.0016196 | 71.0888 | 0.0032482 | [6 empty] | 49023.3023 | 0.003746 | 49023.3023 | 0.00019465 | 49023.3023 | 0.0015414
86.4343 | 0.00070156 | 86.4343 | 0.00070156 | 86.4343 | 0.0032482 | 72.221 | 0.00046635 | 72.221 | 0.0016182 | 72.221 | 0.0032482 | [6 empty] | 49023.5334 | 0.0037461 | 49023.5334 | 0.00019464 | 49023.5334 | 0.0015414
90.6383 | 0.00072957 | 90.6383 | 0.00072957 | 90.6383 | 0.0032482 | 73.6216 | 0.00047146 | 73.6216 | 0.0016164 | 73.6216 | 0.0032482 | [6 empty] | 49023.7977 | 0.0037462 | 49023.7977 | 0.00019462 | 49023.7977 | 0.0015415
96.5662 | 0.00076938 | 96.5662 | 0.00076938 | 96.5662 | 0.0032482 | 75.6387 | 0.0004788 | 75.6387 | 0.0016139 | 75.6387 | 0.0032482 | [6 empty] | 49024.062 | 0.0037464 | 49024.062 | 0.00019461 | 49024.062 | 0.0015415
97.9329 | 0.00077864 | 97.9329 | 0.00077864 | 97.9329 | 0.0032482 | 78.6946 | 0.00048995 | 78.6946 | 0.0016102 | 78.6946 | 0.0032482 | [6 empty] | 49024.3966 | 0.0037465 | 49024.3966 | 0.00019459 | 49024.3966 | 0.0015416
98.2451 | 0.00078076 | 98.2451 | 0.00078076 | 98.2451 | 0.0032482 | 83.3154 | 0.00050683 | 83.3154 | 0.0016047 | 83.3154 | 0.0032482 | [6 empty] | 49024.7313 | 0.0037467 | 49024.7313 | 0.00019458 | 49024.7313 | 0.0015416
98.2898 | 0.00078107 | 98.2898 | 0.00078107 | 98.2898 | 0.0032482 | 91.0315 | 0.0005351 | 91.0315 | 0.0015958 | 91.0315 | 0.0032482 | [6 empty] | 49025.1836 | 0.0037469 | 49025.1836 | 0.00019456 | 49025.1836 | 0.0015417
98.2993 | 0.00078113 | 98.2993 | 0.00078113 | 98.2993 | 0.0032482 | 96.7254 | 0.00055601 | 96.7254 | 0.0015896 | 96.7254 | 0.0032482 | [6 empty] | 49025.6358 | 0.0037471 | 49025.6358 | 0.00019454 | 49025.6358 | 0.0015418
98.3028 | 0.00078115 | 98.3028 | 0.00078115 | 98.3028 | 0.0032482 | 100.1623 | 0.00056849 | 100.1623 | 0.0015857 | 100.1623 | 0.0032482 | [6 empty] | 49026.2711 | 0.0037474 | 49026.2711 | 0.00019453 | 49026.2711 | 0.0015419
98.3029 | 0.00078116 | 98.3029 | 0.00078116 | 98.3029 | 0.0032482 | 100.7602 | 0.00057029 | 100.7602 | 0.0015846 | 100.7602 | 0.0032482 | [6 empty] | 49026.9504 | 0.0037478 | 49026.9504 | 0.00019451 | 49026.9504 | 0.0015421
98.303 | 0.00078116 | 98.303 | 0.00078116 | 98.303 | 0.0032482 | 101.358 | 0.00057194 | 101.358 | 0.0015835 | 101.358 | 0.0032482 | [6 empty] | 49028.3995 | 0.0037485 | 49028.3995 | 0.00019449 | 49028.3995 | 0.0015424
98.3035 | 0.00078116 | 98.3035 | 0.00078116 | 98.3035 | 0.0032482 | 101.9559 | 0.00057348 | 101.9559 | 0.0015824 | 101.9559 | 0.0032482 | [6 empty] | 49029.987 | 0.0037492 | 49029.987 | 0.00019449 | 49029.987 | 0.0015427
98.3047 | 0.00078117 | 98.3047 | 0.00078117 | 98.3047 | 0.0032482 | 103.0547 | 0.00057616 | 103.0547 | 0.0015804 | 103.0547 | 0.0032482 | [6 empty] | 49035.442 | 0.0037519 | 49035.442 | 0.00019453 | 49035.442 | 0.0015437
98.3069 | 0.00078118 | 98.3069 | 0.00078118 | 98.3069 | 0.0032482 | 104.6548 | 0.00057987 | 104.6548 | 0.0015774 | 104.6548 | 0.0032482 | [6 empty] | 49045.6917 | 0.0037572 | 49045.6917 | 0.00019474 | 49045.6917 | 0.0015458
98.3111 | 0.00078121 | 98.3111 | 0.00078121 | 98.3111 | 0.0032482 | 106.773 | 0.00058461 | 106.773 | 0.0015733 | 106.773 | 0.0032482 | [6 empty] | 49059.916 | 0.0037648 | 49059.916 | 0.00019511 | 49059.916 | 0.0015486
98.3193 | 0.00078125 | 98.3193 | 0.00078125 | 98.3193 | 0.0032482 | 109.6928 | 0.00059102 | 109.6928 | 0.0015677 | 109.6928 | 0.0032482 | [6 empty] | 49077.6454 | 0.003775 | 49077.6454 | 0.00019557 | 49077.6454 | 0.0015521
98.336 | 0.00078135 | 98.336 | 0.00078135 | 98.336 | 0.0032482 | 113.3367 | 0.00059891 | 113.3367 | 0.0015608 | 113.3367 | 0.0032482 | [6 empty] | 49103.5333 | 0.0037907 | 49103.5333 | 0.00019621 | 49103.5333 | 0.0015571
98.3701 | 0.00078154 | 98.3701 | 0.00078154 | 98.3701 | 0.0032482 | 118.6308 | 0.00061016 | 118.6308 | 0.0015509 | 118.6308 | 0.0032482 | [6 empty] | 49144.6631 | 0.003817 | 49144.6631 | 0.00019722 | 49144.6631 | 0.0015652
98.4368 | 0.00078193 | 98.4368 | 0.00078193 | 98.4368 | 0.0032482 | 126.8194 | 0.00062708 | 126.8194 | 0.0015362 | 126.8194 | 0.0032482 | [6 empty] | 49196.9095 | 0.0038516 | 49196.9095 | 0.00019852 | 49196.9095 | 0.0015755
98.5578 | 0.00078265 | 98.5578 | 0.00078265 | 98.5578 | 0.0032482 | 129.6674 | 0.00063283 | 129.6674 | 0.0015312 | 129.6674 | 0.0032482 | [6 empty] | 49251.6184 | 0.0038881 | 49251.6184 | 0.00019987 | 49251.6184 | 0.0015862
98.7496 | 0.00078381 | 98.7496 | 0.00078381 | 98.7496 | 0.0032482 | 129.8426 | 0.00063318 | 129.8426 | 0.0015309 | 129.8426 | 0.0032482 | [6 empty] | 49308.2621 | 0.0039252 | 49308.2621 | 0.00020127 | 49308.2621 | 0.0015974
99.0138 | 0.00078541 | 99.0138 | 0.00078541 | 99.0138 | 0.0032482 | 129.8885 | 0.00063327 | 129.8885 | 0.0015308 | 129.8885 | 0.0032482 | [6 empty] | 49370.8888 | 0.0039652 | 49370.8888 | 0.00020282 | 49370.8888 | 0.0016096
99.3658 | 0.00078752 | 99.3658 | 0.00078752 | 99.3658 | 0.0032482 | 130.0465 | 0.00063359 | 130.0465 | 0.0015305 | 130.0465 | 0.0032482 | [6 empty] | 49443.9939 | 0.0040103 | 49443.9939 | 0.00020462 | 49443.9939 | 0.0016239
99.8783 | 0.00079054 | 99.8783 | 0.00079054 | 99.8783 | 0.0032482 | 130.3852 | 0.00063426 | 130.3852 | 0.0015299 | 130.3852 | 0.0032482 | [6 empty] | 49517.0989 | 0.0040539 | 49517.0989 | 0.00020641 | 49517.0989 | 0.0016382
100.5631 | 0.00079405 | 100.5631 | 0.00079405 | 100.5631 | 0.0032482 | 130.7239 | 0.00063494 | 130.7239 | 0.0015293 | 130.7239 | 0.0032482 | [6 empty] | 49615.47 | 0.0041106 | 49615.47 | 0.00020883 | 49615.47 | 0.0016573
101.2479 | 0.00079718 | 101.2479 | 0.00079718 | 101.2479 | 0.0032482 | 131.1769 | 0.00063584 | 131.1769 | 0.0015285 | 131.1769 | 0.0032482 | [6 empty] | 49742.7199 | 0.0041817 | 49742.7199 | 0.00021194 | 49742.7199 | 0.0016821
101.9327 | 0.00080002 | 101.9327 | 0.00080002 | 101.9327 | 0.0032482 | 132.8926 | 0.00063925 | 132.8926 | 0.0015256 | 132.8926 | 0.0032482 | [6 empty] | 49900.3141 | 0.0042673 | 49900.3141 | 0.00021579 | 49900.3141 | 0.0017126
102.8964 | 0.00080364 | 102.8964 | 0.00080364 | 102.8964 | 0.0032482 | 136.6082 | 0.00064655 | 136.6082 | 0.0015193 | 136.6082 | 0.0032482 | [6 empty] | 50097.5574 | 0.0043723 | 50097.5574 | 0.00022058 | 50097.5574 | 0.0017506
104.6942 | 0.00080966 | 104.6942 | 0.00080966 | 104.6942 | 0.0032482 | 142.3296 | 0.0006576 | 142.3296 | 0.0015098 | 142.3296 | 0.0032482 | [6 empty] | 50364.902 | 0.0045122 | 50364.902 | 0.00022704 | 50364.902 | 0.0018019
107.6725 | 0.00081855 | 107.6725 | 0.00081855 | 107.6725 | 0.0032482 | 150.0981 | 0.00067222 | 150.0981 | 0.0014972 | 150.0981 | 0.0032482 | [6 empty] | 50413.5409 | 0.0045359 | 50413.5409 | 0.00022783 | 50413.5409 | 0.0018082
111.2727 | 0.00082847 | 111.2727 | 0.00082847 | 111.2727 | 0.0032482 | 162.7071 | 0.00069513 | 162.7071 | 0.0014777 | 162.7071 | 0.0032482 | [6 empty] | 50453.4864 | 0.0045511 | 50453.4864 | 0.00022764 | 50453.4864 | 0.0018068
115.5449 | 0.00083981 | 115.5449 | 0.00083981 | 115.5449 | 0.0032482 | 178.4758 | 0.00072199 | 178.4758 | 0.0014553 | 178.4758 | 0.0032482 | [6 empty] | 50483.07 | 0.0045592 | 50483.07 | 0.00022749 | 50483.07 | 0.0018056
121.4532 | 0.00085506 | 121.4532 | 0.00085506 | 121.4532 | 0.0032482 | 185.3446 | 0.00073301 | 185.3446 | 0.0014463 | 185.3446 | 0.0032482 | [6 empty] | 50512.6536 | 0.0045648 | 50512.6536 | 0.00022735 | 50512.6536 | 0.0018045
128.4888 | 0.00087259 | 128.4888 | 0.00087259 | 128.4888 | 0.0032482 | 192.2135 | 0.00074361 | 192.2135 | 0.0014375 | 192.2135 | 0.0032482 | [6 empty] | 50557.3862 | 0.0045696 | 50557.3862 | 0.00022714 | 50557.3862 | 0.0018028
129.2863 | 0.00087454 | 129.2863 | 0.00087454 | 129.2863 | 0.0032482 | 199.2907 | 0.00075433 | 199.2907 | 0.0014286 | 199.2907 | 0.0032482 | [6 empty] | 50632.5672 | 0.0045708 | 50632.5672 | 0.00022678 | 50632.5672 | 0.0018
129.3788 | 0.00087476 | 129.3788 | 0.00087476 | 129.3788 | 0.0032482 | 208.6084 | 0.00076819 | 208.6084 | 0.0014172 | 208.6084 | 0.0032482 | [6 empty] | 50721.0008 | 0.0045647 | 50721.0008 | 0.00022636 | 50721.0008 | 0.0017966
129.4487 | 0.00087493 | 129.4487 | 0.00087493 | 129.4487 | 0.0032482 | 229.2223 | 0.00079796 | 229.2223 | 0.0013929 | 229.2223 | 0.0032482 | [6 empty] | 50817.6379 | 0.0045532 | 50817.6379 | 0.00022589 | 50817.6379 | 0.001793
129.6316 | 0.00087538 | 129.6316 | 0.00087538 | 129.6316 | 0.0032482 | 244.6862 | 0.00081951 | 244.6862 | 0.0013755 | 244.6862 | 0.0032482 | [6 empty] | 50936.1508 | 0.004536 | 50936.1508 | 0.00022532 | 50936.1508 | 0.0017884
129.9663 | 0.00087619 | 129.9663 | 0.00087619 | 129.9663 | 0.0032482 | 267.0668 | 0.00084974 | 267.0668 | 0.0013514 | 267.0668 | 0.0032482 | [6 empty] | 51094.2125 | 0.0045116 | 51094.2125 | 0.00022457 | 51094.2125 | 0.0017824
130.3458 | 0.0008771 | 130.3458 | 0.0008771 | 130.3458 | 0.0032482 | 294.99 | 0.000886 | 294.99 | 0.001323 | 294.99 | 0.0032482 | [6 empty] | 51306.0495 | 0.0044795 | 51306.0495 | 0.00022355 | 51306.0495 | 0.0017743
130.9052 | 0.00087845 | 130.9052 | 0.00087845 | 130.9052 | 0.0032482 | 309.0298 | 0.00090364 | 309.0298 | 0.0013093 | 309.0298 | 0.0032482 | [6 empty] | 51589.2378 | 0.0044393 | 51589.2378 | 0.00022219 | 51589.2378 | 0.0017635
132.7198 | 0.00088279 | 132.7198 | 0.00088279 | 132.7198 | 0.0032482 | 336.6781 | 0.00093741 | 336.6781 | 0.0012835 | 336.6781 | 0.0032482 | [6 empty] | 51986.5573 | 0.0043876 | 51986.5573 | 0.00022028 | 51986.5573 | 0.0017483
137.1868 | 0.00089324 | 137.1868 | 0.00089324 | 137.1868 | 0.0032482 | 375.4604 | 0.00098265 | 375.4604 | 0.0012496 | 375.4604 | 0.0032482 | [6 empty] | 52699.1527 | 0.0043028 | 52699.1527 | 0.00021684 | 52699.1527 | 0.001721
143.3303 | 0.00090714 | 143.3303 | 0.00090714 | 143.3303 | 0.0032482 | 426.1575 | 0.0010377 | 426.1575 | 0.0012092 | 426.1575 | 0.0032482 | [6 empty] | 53632.7165 | 0.0041995 | 53632.7165 | 0.00021231 | 53632.7165 | 0.0016851
151.3634 | 0.00092467 | 151.3634 | 0.00092467 | 151.3634 | 0.0032482 | 440.7327 | 0.0010525 | 440.7327 | 0.0011988 | 440.7327 | 0.0032482 | [6 empty] | 54158.038 | 0.0041363 | 54158.038 | 0.00020934 | 54158.038 | 0.0016615
159.5357 | 0.00094164 | 159.5357 | 0.00094164 | 159.5357 | 0.0032482 | 458.6749 | 0.0010697 | 458.6749 | 0.0011867 | 458.6749 | 0.0032482 | [6 empty] | 54569.5867 | 0.0040723 | 54569.5867 | 0.00020622 | 54569.5867 | 0.0016368
164.9294 | 0.0009527 | 164.9294 | 0.0009527 | 164.9294 | 0.0032482 | 476.6172 | 0.0010864 | 476.6172 | 0.001175 | 476.6172 | 0.0032482 | [6 empty] | 54865.8703 | 0.0040213 | 54865.8703 | 0.00020398 | 54865.8703 | 0.001619
171.3175 | 0.00096516 | 171.3175 | 0.00096516 | 171.3175 | 0.0032482 | 494.5595 | 0.0011027 | 494.5595 | 0.0011637 | 494.5595 | 0.0032482 | [6 empty] | 55162.154 | 0.0039699 | 55162.154 | 0.00020172 | 55162.154 | 0.0016011
177.7055 | 0.00097734 | 177.7055 | 0.00097734 | 177.7055 | 0.0032482 | 514.0398 | 0.00112 | 514.0398 | 0.0011518 | 514.0398 | 0.0032482 | [6 empty] | 55504.2835 | 0.0039112 | 55504.2835 | 0.00019912 | 55504.2835 | 0.0015804
184.2551 | 0.00098961 | 184.2551 | 0.00098961 | 184.2551 | 0.0032482 | 520.8766 | 0.0011259 | 520.8766 | 0.0011478 | 520.8766 | 0.0032482 | [6 empty] | 56186.9009 | 0.0037945 | 56186.9009 | 0.0001939 | 56186.9009 | 0.001539
190.8047 | 0.0010016 | 190.8047 | 0.0010016 | 190.8047 | 0.0032482 | 521.975 | 0.0011268 | 521.975 | 0.0011472 | 521.975 | 0.0032482 | [6 empty] | 57391.617 | 0.0035866 | 57391.617 | 0.00018462 | 57391.617 | 0.0014653
202.3688 | 0.0010222 | 202.3688 | 0.0010222 | 202.3688 | 0.0032482 | 522.1947 | 0.001127 | 522.1947 | 0.001147 | 522.1947 | 0.0032482 | [6 empty] | 57473.1833 | 0.0035725 | 57473.1833 | 0.00018399 | 57473.1833 | 0.0014603
225.2808 | 0.0010611 | 225.2808 | 0.0010611 | 225.2808 | 0.0032482 | 522.2738 | 0.0011271 | 522.2738 | 0.001147 | 522.2738 | 0.0032482 | [6 empty] | 57497.5914 | 0.0035682 | 57497.5914 | 0.0001838 | 57497.5914 | 0.0014588
248.1929 | 0.0010979 | 248.1929 | 0.0010979 | 248.1929 | 0.0032482 | 522.3023 | 0.0011271 | 522.3023 | 0.001147 | 522.3023 | 0.0032482 | [6 empty] | 57505.2138 | 0.0035669 | 57505.2138 | 0.00018374 | 57505.2138 | 0.0014584
271.105 | 0.0011329 | 271.105 | 0.0011329 | 271.105 | 0.0032482 | 522.3042 | 0.0011271 | 522.3042 | 0.001147 | 522.3042 | 0.0032482 | [6 empty] | 57514.914 | 0.0035652 | 57514.914 | 0.00018363 | 57514.914 | 0.0014577
294.5198 | 0.0011672 | 294.5198 | 0.0011672 | 294.5198 | 0.0032482 | 522.3209 | 0.0011271 | 522.3209 | 0.001147 | 522.3209 | 0.0032482 | [6 empty] | 57524.6143 | 0.0035636 | 57524.6143 | 0.00018354 | 57524.6143 | 0.0014571
317.9346 | 0.0012 | 317.9346 | 0.0012 | 317.9346 | 0.0032482 | 522.363 | 0.0011272 | 522.363 | 0.0011469 | 522.363 | 0.0032482 | [6 empty] | 57554.8808 | 0.0035586 | 57554.8808 | 0.00018329 | 57554.8808 | 0.0014552
348.9847 | 0.0012409 | 348.9847 | 0.0012409 | 348.9847 | 0.0032482 | 522.4307 | 0.0011272 | 522.4307 | 0.0011469 | 522.4307 | 0.0032482 | [6 empty] | 57611.1602 | 0.0035492 | 57611.1602 | 0.00018271 | 57611.1602 | 0.0014508
355.1331 | 0.0012489 | 355.1331 | 0.0012489 | 355.1331 | 0.0032482 | 522.543 | 0.0011273 | 522.543 | 0.0011468 | 522.543 | 0.0032482 | [6 empty] | 57674.4211 | 0.0035362 | 57674.4211 | 0.00018148 | 57674.4211 | 0.0014416
363.7347 | 0.0012595 | 363.7347 | 0.0012595 | 363.7347 | 0.0032482 | 522.7843 | 0.0011275 | 522.7843 | 0.0011466 | 522.7843 | 0.0032482 | [6 empty] | 57737.6819 | 0.0035205 | 57737.6819 | 0.00018029 | 57737.6819 | 0.0014324
372.3363 | 0.0012699 | 372.3363 | 0.0012699 | 372.3363 | 0.0032482 | 523.5292 | 0.001128 | 523.5292 | 0.0011462 | 523.5292 | 0.0032482 | [6 empty] | 57800.9428 | 0.0035027 | 57800.9428 | 0.00017911 | 57800.9428 | 0.0014232
380.9379 | 0.0012803 | 380.9379 | 0.0012803 | 380.9379 | 0.0032482 | 524.7763 | 0.0011289 | 524.7763 | 0.0011454 | 524.7763 | 0.0032482 | [6 empty] | 57876.6649 | 0.0034797 | 57876.6649 | 0.00017769 | 57876.6649 | 0.0014121
390.1485 | 0.0012914 | 390.1485 | 0.0012914 | 390.1485 | 0.0032482 | 526.3776 | 0.0011301 | 526.3776 | 0.0011444 | 526.3776 | 0.0032482 | [6 empty] | 58021.8606 | 0.003433 | 58021.8606 | 0.00017495 | 58021.8606 | 0.0013907
399.8048 | 0.0013028 | 399.8048 | 0.0013028 | 399.8048 | 0.0032482 | 528.808 | 0.0011319 | 528.808 | 0.0011428 | 528.808 | 0.0032482 | [6 empty] | 58153.8233 | 0.0033889 | 58153.8233 | 0.00017247 | 58153.8233 | 0.0013712
418.0093 | 0.0013238 | 418.0093 | 0.0013238 | 418.0093 | 0.0032482 | 535.041 | 0.0011363 | 535.041 | 0.001139 | 535.041 | 0.0032482 | [6 empty] | 58287.075 | 0.0033436 | 58287.075 | 0.00016995 | 58287.075 | 0.0013514
457.4755 | 0.0013675 | 457.4755 | 0.0013675 | 457.4755 | 0.0032482 | 554.903 | 0.0011504 | 554.903 | 0.0011267 | 554.903 | 0.0032482 | [6 empty] | 58390.6422 | 0.0033081 | 58390.6422 | 0.00016799 | 58390.6422 | 0.001336
496.9418 | 0.001409 | 496.9418 | 0.001409 | 496.9418 | 0.0032482 | 578.5439 | 0.0011668 | 578.5439 | 0.0011124 | 578.5439 | 0.0032482 | [6 empty] | 58491.8044 | 0.0032731 | 58491.8044 | 0.00016608 | 58491.8044 | 0.0013209
545.9157 | 0.0014576 | 545.9157 | 0.0014576 | 545.9157 | 0.0032482 | 589.4815 | 0.0011742 | 589.4815 | 0.001106 | 589.4815 | 0.0032482 | [6 empty] | 58607.1863 | 0.0032328 | 58607.1863 | 0.0001639 | 58607.1863 | 0.0013037
585.374 | 0.0014942 | 585.374 | 0.0014942 | 585.374 | 0.0032482 | 618.6943 | 0.0011934 | 618.6943 | 0.0010892 | 618.6943 | 0.0032482 | [6 empty] | 58701.3602 | 0.0031995 | 58701.3602 | 0.00016212 | 58701.3602 | 0.0012896
660.0093 | 0.0015576 | 660.0093 | 0.0015576 | 660.0093 | 0.0032482 | 657.9029 | 0.0012178 | 657.9029 | 0.0010677 | 657.9029 | 0.0032482 | [6 empty] | 58824.4968 | 0.0031554 | 58824.4968 | 0.00015979 | 58824.4968 | 0.0012712
688.2986 | 0.0015797 | 688.2986 | 0.0015797 | 688.2986 | 0.0032482 | 674.1961 | 0.0012275 | 674.1961 | 0.0010591 | 674.1961 | 0.0032482 | [6 empty] | 59035.1408 | 0.0030788 | 59035.1408 | 0.00015581 | 59035.1408 | 0.0012397
717.7319 | 0.0015999 | 717.7319 | 0.0015999 | 717.7319 | 0.0032482 | 724.0286 | 0.0012557 | 724.0286 | 0.0010343 | 724.0286 | 0.0032482 | [6 empty] | 59109.3209 | 0.0030515 | 59109.3209 | 0.0001544 | 59109.3209 | 0.0012285
720.1647 | 0.0016014 | 720.1647 | 0.0016014 | 720.1647 | 0.0032482 | 821.1237 | 0.0013048 | 821.1237 | 0.00099137 | 821.1237 | 0.0032482 | [6 empty] | 59208.2842 | 0.0030146 | 59208.2842 | 0.00015252 | 59208.2842 | 0.0012137
721.4126 | 0.0016023 | 721.4126 | 0.0016023 | 721.4126 | 0.0032482 | 885.2064 | 0.0013329 | 885.2064 | 0.0009669 | 885.2064 | 0.0032482 | [6 empty] | 59303.2753 | 0.0029787 | 59303.2753 | 0.00015072 | 59303.2753 | 0.0011994
724.2464 | 0.0016039 | 724.2464 | 0.0016039 | 724.2464 | 0.0032482 | 971.607 | 0.001366 | 971.607 | 0.00093808 | 971.607 | 0.0032482 | [6 empty] | 59455.2001 | 0.0029203 | 59455.2001 | 0.00014784 | 59455.2001 | 0.0011766
730.3842 | 0.001607 | 730.3842 | 0.001607 | 730.3842 | 0.0032482 | 1022.9894 | 0.0013826 | 1022.9894 | 0.0009236 | 1022.9894 | 0.0032482 | [6 empty] | 59598.079 | 0.0028643 | 59598.079 | 0.00014513 | 59598.079 | 0.0011551
736.5219 | 0.0016098 | 736.5219 | 0.0016098 | 736.5219 | 0.0032482 | 1032.7391 | 0.0013856 | 1032.7391 | 0.00092113 | 1032.7391 | 0.0032482 | [6 empty] | 59741.7789 | 0.0028072 | 59741.7789 | 0.0001424 | 59741.7789 | 0.0011335
743.3644 | 0.0016131 | 743.3644 | 0.0016131 | 743.3644 | 0.0032482 | 1049.2309 | 0.0013904 | 1049.2309 | 0.00091707 | 1049.2309 | 0.0032482 | [6 empty] | 59898.6075 | 0.0027439 | 59898.6075 | 0.00013943 | 59898.6075 | 0.0011098
756.7501 | 0.0016196 | 756.7501 | 0.0016196 | 756.7501 | 0.0032482 | 1072.0445 | 0.0013968 | 1072.0445 | 0.00091168 | 1072.0445 | 0.0032482 | [6 empty] | 60050.4454 | 0.0026819 | 60050.4454 | 0.00013655 | 60050.4454 | 0.001087
778.9692 | 0.0016305 | 778.9692 | 0.0016305 | 778.9692 | 0.0032482 | 1119.0266 | 0.0014095 | 1119.0266 | 0.00090119 | 1119.0266 | 0.0032482 | [6 empty] | 60277.8283 | 0.002588 | 60277.8283 | 0.00013222 | 60277.8283 | 0.0010527
816.8234 | 0.0016488 | 816.8234 | 0.0016488 | 816.8234 | 0.0032482 | 1145.9822 | 0.0014164 | 1145.9822 | 0.00089557 | 1145.9822 | 0.0032482 | [6 empty] | 60393.2601 | 0.0025396 | 60393.2601 | 0.00013002 | 60393.2601 | 0.0010352
864.4163 | 0.0016714 | 864.4163 | 0.0016714 | 864.4163 | 0.0032482 | 1147.8236 | 0.0014168 | 1147.8236 | 0.0008952 | 1147.8236 | 0.0032482 | [6 empty] | 60585.2468 | 0.0024582 | 60585.2468 | 0.00012636 | 60585.2468 | 0.0010062
915.7636 | 0.0016948 | 915.7636 | 0.0016948 | 915.7636 | 0.0032482 | 1152.0679 | 0.0014177 | 1152.0679 | 0.00089433 | 1152.0679 | 0.0032482 | [6 empty] | 60747.1072 | 0.0023889 | 60747.1072 | 0.00012328 | 60747.1072 | 0.00098176
974.4794 | 0.0017203 | 974.4794 | 0.0017203 | 974.4794 | 0.0032482 | 1159.807 | 0.001419 | 1159.807 | 0.00089275 | 1159.807 | 0.0032482 | [6 empty] | 60893.6334 | 0.0023258 | 60893.6334 | 0.00012049 | 60893.6334 | 0.00095959
1026.0673 | 0.0017416 | 1026.0673 | 0.0017416 | 1026.0673 | 0.0032482 | 1167.546 | 0.0014203 | 1167.546 | 0.00089117 | 1167.546 | 0.0032482 | [6 empty] | 61101.3607 | 0.0022364 | 61101.3607 | 0.00011653 | 61101.3607 | 0.00092813
1037.7427 | 0.0017462 | 1037.7427 | 0.0017462 | 1037.7427 | 0.0032482 | 1179.6673 | 0.0014223 | 1179.6673 | 0.0008887 | 1179.6673 | 0.0032482 | [6 empty] | 61204.4292 | 0.0021923 | 61204.4292 | 0.00011463 | 61204.4292 | 0.00091298
1040.0464 | 0.0017471 | 1040.0464 | 0.0017471 | 1040.0464 | 0.0032482 | 1210.1291 | 0.0014273 | 1210.1291 | 0.00088256 | 1210.1291 | 0.0032482 | [6 empty] | 61229.676 | 0.0021822 | 61229.676 | 0.00011454 | 61229.676 | 0.00091178
1043.7913 | 0.0017482 | 1043.7913 | 0.0017482 | 1043.7913 | 0.0032482 | 1259.97 | 0.0014353 | 1259.97 | 0.00087282 | 1259.97 | 0.0032482 | [6 empty] | 61254.9229 | 0.0021729 | 61254.9229 | 0.00011442 | 61254.9229 | 0.00091062
1048.8126 | 0.0017491 | 1048.8126 | 0.0017491 | 1048.8126 | 0.0032482 | 1325.9352 | 0.0014453 | 1325.9352 | 0.00086066 | 1325.9352 | 0.0032482 | [6 empty] | 61280.1698 | 0.0021644 | 61280.1698 | 0.00011427 | 61280.1698 | 0.00090944
1050.676 | 0.0017493 | 1050.676 | 0.0017493 | 1050.676 | 0.0032482 | 1376.6296 | 0.0014525 | 1376.6296 | 0.00085194 | 1376.6296 | 0.0032482 | [6 empty] | 61311.8656 | 0.0021548 | 61311.8656 | 0.00011409 | 61311.8656 | 0.00090797
1051.0452 | 0.0017494 | 1051.0452 | 0.0017494 | 1051.0452 | 0.0032482 | 1454.8356 | 0.0014626 | 1454.8356 | 0.00083955 | 1454.8356 | 0.0032482 | [6 empty] | 61391.5862 | 0.0021339 | 61391.5862 | 0.00011366 | 61391.5862 | 0.0009043
1051.6825 | 0.0017501 | 1051.6825 | 0.0017501 | 1051.6825 | 0.0032482 | 1533.4821 | 0.0014717 | 1533.4821 | 0.00082829 | 1533.4821 | 0.0032482 | [6 empty] | 61525.5648 | 0.0021057 | 61525.5648 | 0.00011292 | 61525.5648 | 0.00089816
1052.0733 | 0.0017504 | 1052.0733 | 0.0017504 | 1052.0733 | 0.0032482 | 1556.3612 | 0.0014742 | 1556.3612 | 0.00082524 | 1556.3612 | 0.0032482 | [6 empty] | 61697.764 | 0.0020764 | 61697.764 | 0.00011197 | 61697.764 | 0.00089036
1052.4642 | 0.0017506 | 1052.4642 | 0.0017506 | 1052.4642 | 0.0032482 | 1561.2353 | 0.0014746 | 1561.2353 | 0.0008246 | 1561.2353 | 0.0032482 | [6 empty] | 61884.2222 | 0.0020489 | 61884.2222 | 0.00011094 | 61884.2222 | 0.00088199
1052.855 | 0.0017509 | 1052.855 | 0.0017509 | 1052.855 | 0.0032482 | 1575.3926 | 0.0014753 | 1575.3926 | 0.00082274 | 1575.3926 | 0.0032482 | [6 empty] | 62126.8288 | 0.002016 | 62126.8288 | 0.0001096 | 62126.8288 | 0.00087119
1053.8137 | 0.0017515 | 1053.8137 | 0.0017515 | 1053.8137 | 0.0032482 | 1576.4349 | 0.0014753 | 1576.4349 | 0.00082261 | 1576.4349 | 0.0032482 | [6 empty] | 62416.4435 | 0.001979 | 62416.4435 | 0.00010801 | 62416.4435 | 0.00085836
1055.2766 | 0.0017524 | 1055.2766 | 0.0017524 | 1055.2766 | 0.0032482 | 1576.7029 | 0.0014754 | 1576.7029 | 0.00082261 | 1576.7029 | 0.0032482 | [6 empty] | 62731.3302 | 0.0019402 | 62731.3302 | 0.00010627 | 62731.3302 | 0.00084448
1057.3638 | 0.0017535 | 1057.3638 | 0.0017535 | 1057.3638 | 0.0032482 | 1577.1254 | 0.0014754 | 1577.1254 | 0.00082261 | 1577.1254 | 0.0032482 | [6 empty] | 63079.5536 | 0.0018982 | 63079.5536 | 0.00010435 | 63079.5536 | 0.00082917
1061.6358 | 0.0017555 | 1061.6358 | 0.0017555 | 1061.6358 | 0.0032482 | 1577.5479 | 0.0014755 | 1577.5479 | 0.00082258 | 1577.5479 | 0.0032482 | [6 empty] | 63482.423 | 0.0018499 | 63482.423 | 0.00010212 | 63482.423 | 0.00081147
1070.8845 | 0.0017587 | 1070.8845 | 0.0017587 | 1070.8845 | 0.0032482 | 1578.6285 | 0.0014757 | 1578.6285 | 0.0008225 | 1578.6285 | 0.0032482 | [6 empty] | 63980.5513 | 0.0017905 | 63980.5513 | 9.9366e-05 | 63980.5513 | 0.00078959
1081.8636 | 0.0017618 | 1081.8636 | 0.0017618 | 1081.8636 | 0.0032482 | 1579.8063 | 0.0014759 | 1579.8063 | 0.00082243 | 1579.8063 | 0.0032482 | [6 empty] | 64620.5769 | 0.0017144 | 64620.5769 | 9.5824e-05 | 64620.5769 | 0.00076146
1092.8428 | 0.0017647 | 1092.8428 | 0.0017647 | 1092.8428 | 0.0032482 | 1581.5149 | 0.0014762 | 1581.5149 | 0.00082232 | 1581.5149 | 0.0032482 | [6 empty] | 64778.5373 | 0.0016954 | 64778.5373 | 9.4948e-05 | 64778.5373 | 0.00075451
1107.8445 | 0.0017687 | 1107.8445 | 0.0017687 | 1107.8445 | 0.0032482 | 1586.6259 | 0.001477 | 1586.6259 | 0.000822 | 1586.6259 | 0.0032482 | [6 empty] | 64826.4331 | 0.0016889 | 64826.4331 | 9.4389e-05 | 64826.4331 | 0.00075037
1134.0881 | 0.0017759 | 1134.0881 | 0.0017759 | 1134.0881 | 0.0032482 | 1599.0678 | 0.0014787 | 1599.0678 | 0.00082127 | 1599.0678 | 0.0032482 | [6 empty] | 64874.3289 | 0.0016807 | 64874.3289 | 9.3621e-05 | 64874.3289 | 0.00074458
1160.8709 | 0.0017836 | 1160.8709 | 0.0017836 | 1160.8709 | 0.0032482 | 1621.1189 | 0.0014816 | 1621.1189 | 0.00082007 | 1621.1189 | 0.0032482 | [6 empty] | 64926.7806 | 0.0016698 | 64926.7806 | 9.2814e-05 | 64926.7806 | 0.00073823
1173.1822 | 0.0017874 | 1173.1822 | 0.0017874 | 1173.1822 | 0.0032482 | 1644.2521 | 0.0014844 | 1644.2521 | 0.0008189 | 1644.2521 | 0.0032482 | [6 empty] | 64979.2323 | 0.0016572 | 64979.2323 | 9.2005e-05 | 64979.2323 | 0.00073186
1181.2025 | 0.0017903 | 1181.2025 | 0.0017903 | 1181.2025 | 0.0032482 | 1652.6023 | 0.0014852 | 1652.6023 | 0.00081855 | 1652.6023 | 0.0032482 | [6 empty] | 65067.3793 | 0.0016338 | 65067.3793 | 9.0637e-05 | 65067.3793 | 0.00072114
1187.0957 | 0.0017933 | 1187.0957 | 0.0017933 | 1187.0957 | 0.0032482 | 1667.5387 | 0.0014863 | 1667.5387 | 0.00081807 | 1667.5387 | 0.0032482 | [6 empty] | 65260.5651 | 0.0015769 | 65260.5651 | 8.7637e-05 | 65260.5651 | 0.00069755
1191.4477 | 0.001796 | 1191.4477 | 0.001796 | 1191.4477 | 0.0032482 | 1691.1407 | 0.0014875 | 1691.1407 | 0.00081747 | 1691.1407 | 0.0032482 | [6 empty] | 65543.809 | 0.0014872 | 65543.809 | 8.3233e-05 | 65543.809 | 0.0006628
1195.7996 | 0.0017991 | 1195.7996 | 0.0017991 | 1195.7996 | 0.0032482 | 1714.7427 | 0.0014886 | 1714.7427 | 0.00081689 | 1714.7427 | 0.0032482 | [6 empty] | 65855.2479 | 0.0013865 | 65855.2479 | 7.8382e-05 | 65855.2479 | 0.00062439
1202.5888 | 0.0018039 | 1202.5888 | 0.0018039 | 1202.5888 | 0.0032482 | 1746.1426 | 0.0014902 | 1746.1426 | 0.0008161 | 1746.1426 | 0.0032482 | [6 empty] | 66172.1794 | 0.0012852 | 66172.1794 | 7.3429e-05 | 66172.1794 | 0.00058514
1209.378 | 0.0018087 | 1209.378 | 0.0018087 | 1209.378 | 0.0032482 | 1802.8772 | 0.001493 | 1802.8772 | 0.00081466 | 1802.8772 | 0.0032482 | [6 empty] | 66506.2681 | 0.001181 | 66506.2681 | 6.8195e-05 | 66506.2681 | 0.00054358
1220.4166 | 0.0018165 | 1220.4166 | 0.0018165 | 1220.4166 | 0.0032482 | 1874.9925 | 0.0014969 | 1874.9925 | 0.00081276 | 1874.9925 | 0.0032482 | [6 empty] | 66882.6657 | 0.0010662 | 66882.6657 | 6.227e-05 | 66882.6657 | 0.00049649
1244.9103 | 0.0018338 | 1244.9103 | 0.0018338 | 1244.9103 | 0.0032482 | 1911.9043 | 0.0014993 | 1911.9043 | 0.00081161 | 1911.9043 | 0.0032482 | [6 empty] | 67314.367 | 0.00093814 | 67314.367 | 5.5433e-05 | 67314.367 | 0.00044212
1282.576 | 0.0018608 | 1282.576 | 0.0018608 | 1282.576 | 0.0032482 | 1958.7094 | 0.0015047 | 1958.7094 | 0.00080929 | 1958.7094 | 0.0032482 | [6 empty] | 67822.8405 | 0.00079342 | 67822.8405 | 4.7312e-05 | 67822.8405 | 0.00037745
1342.1586 | 0.0019039 | 1342.1586 | 0.0019039 | 1342.1586 | 0.0032482 | 1985.9919 | 0.0015082 | 1985.9919 | 0.00080786 | 1985.9919 | 0.0032482 | [6 empty] | 68355.949 | 0.00064749 | 68355.949 | 3.8691e-05 | 68355.949 | 0.00030873
1369.809 | 0.0019234 | 1369.809 | 0.0019234 | 1369.809 | 0.0032482 | 2013.2744 | 0.0015115 | 2013.2744 | 0.00080647 | 2013.2744 | 0.0032482 | [6 empty] | 68384.3273 | 0.00063987 | 68384.3273 | 3.823e-05 | 68384.3273 | 0.00030504
1382.7511 | 0.0019323 | 1382.7511 | 0.0019323 | 1382.7511 | 0.0032482 | 2045.6648 | 0.0015154 | 2045.6648 | 0.00080485 | 2045.6648 | 0.0032482 | [6 empty] | 68397.701 | 0.00063628 | 68397.701 | 3.8011e-05 | 68397.701 | 0.0003033
1404.4291 | 0.0019472 | 1404.4291 | 0.0019472 | 1404.4291 | 0.0032482 | 2112.9815 | 0.0015233 | 2112.9815 | 0.00080159 | 2112.9815 | 0.0032482 | [6 empty] | 68401.7274 | 0.00063521 | 68401.7274 | 3.8025e-05 | 68401.7274 | 0.00030344
1442.5426 | 0.0019735 | 1442.5426 | 0.0019735 | 1442.5426 | 0.0032482 | 2244.3253 | 0.0015378 | 2244.3253 | 0.00079562 | 2244.3253 | 0.0032482 | [6 empty] | 68405.7538 | 0.00063421 | 68405.7538 | 3.8171e-05 | 68405.7538 | 0.00030451
1499.3824 | 0.0020128 | 1499.3824 | 0.0020128 | 1499.3824 | 0.0032482 | 2429.5349 | 0.0015559 | 2429.5349 | 0.00078809 | 2429.5349 | 0.0032482 | [6 empty] | 68409.5633 | 0.00063333 | 68409.5633 | 3.8338e-05 | 68409.5633 | 0.00030555
1557.2026 | 0.0020528 | 1557.2026 | 0.0020528 | 1557.2026 | 0.0032482 | 2683.4761 | 0.0015766 | 2683.4761 | 0.00077931 | 2683.4761 | 0.0032482 | [6 empty] | 68413.3729 | 0.00063253 | 68413.3729 | 3.8495e-05 | 68413.3729 | 0.00030656
1642.6386 | 0.0021118 | 1642.6386 | 0.0021118 | 1642.6386 | 0.0032482 | 3145.19 | 0.0016035 | 3145.19 | 0.00076729 | 3145.19 | 0.0032482 | [6 empty] | 68423.1517 | 0.00063084 | 68423.1517 | 3.8865e-05 | 68423.1517 | 0.00030916
1705.6545 | 0.0021553 | 1705.6545 | 0.0021553 | 1705.6545 | 0.0032482 | 3499.3099 | 0.0016153 | 3499.3099 | 0.00076118 | 3499.3099 | 0.0032482 | [6 empty] | 68440.2953 | 0.00062901 | 68440.2953 | 3.9467e-05 | 68440.2953 | 0.00031371
1736.2706 | 0.0021763 | 1736.2706 | 0.0021763 | 1736.2706 | 0.0032482 | 3611.5647 | 0.0016177 | 3611.5647 | 0.00075976 | 3611.5647 | 0.0032482 | [6 empty] | 68466.2687 | 0.00062866 | 68466.2687 | 4.0352e-05 | 68466.2687 | 0.00032058
1747.2343 | 0.0021839 | 1747.2343 | 0.0021839 | 1747.2343 | 0.0032482 | 3653.2753 | 0.0016188 | 3653.2753 | 0.00075937 | 3653.2753 | 0.0032482 | [6 empty] | 68506.3216 | 0.00063276 | 68506.3216 | 4.1713e-05 | 68506.3216 | 0.00033115
1749.2669 | 0.0021853 | 1749.2669 | 0.0021853 | 1749.2669 | 0.0032482 | 3687.838 | 0.0016197 | 3687.838 | 0.00075905 | 3687.838 | 0.0032482 | [6 empty] | 68577.8138 | 0.00065003 | 68577.8138 | 4.4137e-05 | 68577.8138 | 0.00034995
1754.9634 | 0.0021892 | 1754.9634 | 0.0021892 | 1754.9634 | 0.0032482 | 3722.4006 | 0.0016206 | 3722.4006 | 0.00075872 | 3722.4006 | 0.0032482 | [6 empty] | 68718.9452 | 0.00070483 | 68718.9452 | 4.8879e-05 | 68718.9452 | 0.00038679
1769.0179 | 0.0021988 | 1769.0179 | 0.0021988 | 1769.0179 | 0.0032482 | 3791.5974 | 0.0016225 | 3791.5974 | 0.00075808 | 3791.5974 | 0.0032482 | [6 empty] | 68890.0356 | 0.00078976 | 68890.0356 | 5.4554e-05 | 68890.0356 | 0.00043101
1783.0724 | 0.0022085 | 1783.0724 | 0.0022085 | 1783.0724 | 0.0032482 | 3909.8957 | 0.0016255 | 3909.8957 | 0.00075701 | 3909.8957 | 0.0032482 | [6 empty] | 69077.7861 | 0.00089064 | 69077.7861 | 6.0705e-05 | 69077.7861 | 0.00047906
1797.1269 | 0.0022181 | 1797.1269 | 0.0022181 | 1797.1269 | 0.0032482 | 4065.9013 | 0.0016293 | 4065.9013 | 0.00075569 | 4065.9013 | 0.0032482 | [6 empty] | 69298.3179 | 0.0010123 | 69298.3179 | 6.7846e-05 | 69298.3179 | 0.00053501
1937.672 | 0.0023139 | 1937.672 | 0.0023139 | 1937.672 | 0.0032482 | 4273.8377 | 0.0016339 | 4273.8377 | 0.00075406 | 4273.8377 | 0.0032482 | [6 empty] | 69520.9526 | 0.0011392 | 69520.9526 | 7.4989e-05 | 69520.9526 | 0.00059112
1945.9203 | 0.0023195 | 1945.9203 | 0.0023195 | 1945.9203 | 0.0032482 | 4608.2001 | 0.0016404 | 4608.2001 | 0.00075175 | 4608.2001 | 0.0032482 | [6 empty] | 69743.5873 | 0.001272 | 69743.5873 | 8.2071e-05 | 69743.5873 | 0.00064698
1947.1187 | 0.0023203 | 1947.1187 | 0.0023203 | 1947.1187 | 0.0032482 | 5316.502 | 0.0016513 | 5316.502 | 0.00074782 | 5316.502 | 0.0032482 | [6 empty] | 69966.222 | 0.001411 | 69966.222 | 8.9133e-05 | 69966.222 | 0.00070265
1947.1313 | 0.0023203 | 1947.1313 | 0.0023203 | 1947.1313 | 0.0032482 | 6230.1073 | 0.0016608 | 6230.1073 | 0.00074425 | 6230.1073 | 0.0032482 | [6 empty] | 70198.2543 | 0.0015617 | 70198.2543 | 9.6454e-05 | 70198.2543 | 0.00076052
1947.1413 | 0.0023204 | 1947.1413 | 0.0023204 | 1947.1413 | 0.0032482 | 7143.7127 | 0.0016667 | 7143.7127 | 0.00074186 | 7143.7127 | 0.0032482 | [6 empty] | 70447.6588 | 0.0017313 | 70447.6588 | 0.0001043 | 70447.6588 | 0.00082264
1947.1501 | 0.0023204 | 1947.1501 | 0.0023204 | 1947.1501 | 0.0032482 | 8057.318 | 0.0016703 | 8057.318 | 0.00074022 | 8057.318 | 0.0032482 | [6 empty] | 70719.2917 | 0.0019241 | 70719.2917 | 0.00011283 | 70719.2917 | 0.00089021
1947.1556 | 0.0023204 | 1947.1556 | 0.0023204 | 1947.1556 | 0.0032482 | 8970.9233 | 0.0016725 | 8970.9233 | 0.00073905 | 8970.9233 | 0.0032482 | [6 empty] | 71009.9425 | 0.0021356 | 71009.9425 | 0.00012193 | 71009.9425 | 0.00096238
1947.1611 | 0.0023204 | 1947.1611 | 0.0023204 | 1947.1611 | 0.0032482 | 10109.8794 | 0.001674 | 10109.8794 | 0.00073796 | 10109.8794 | 0.0032482 | [6 empty] | 71159.9855 | 0.0022467 | 71159.9855 | 0.00012662 | 71159.9855 | 0.00099962
1947.1631 | 0.0023204 | 1947.1631 | 0.0023204 | 1947.1631 | 0.0032482 | 11545.7595 | 0.0016749 | 11545.7595 | 0.00073693 | 11545.7595 | 0.0032482 | [6 empty] | 71299.6118 | 0.0023514 | 71299.6118 | 0.00013099 | 71299.6118 | 0.0010343
1947.1651 | 0.0023204 | 1947.1651 | 0.0023204 | 1947.1651 | 0.0032482 | 13273.7595 | 0.0016751 | 13273.7595 | 0.00073596 | 13273.7595 | 0.0032482 | [6 empty] | 71457.3948 | 0.0024699 | 71457.3948 | 0.00013591 | 71457.3948 | 0.0010734
1947.1672 | 0.0023204 | 1947.1672 | 0.0023204 | 1947.1672 | 0.0032482 | 15001.7595 | 0.0016749 | 15001.7595 | 0.00073513 | 15001.7595 | 0.0032482 | [6 empty] | 71550.1246 | 0.0025393 | 71550.1246 | 0.00013881 | 71550.1246 | 0.0010963
1947.1692 | 0.0023204 | 1947.1692 | 0.0023204 | 1947.1692 | 0.0032482 | 16729.7595 | 0.0016746 | 16729.7595 | 0.00073435 | 16729.7595 | 0.0032482 | [6 empty] | 71737.644 | 0.002679 | 71737.644 | 0.00014466 | 71737.644 | 0.0011428
1947.1731 | 0.0023204 | 1947.1731 | 0.0023204 | 1947.1731 | 0.0032482 | 18457.7595 | 0.0016742 | 18457.7595 | 0.0007336 | 18457.7595 | 0.0032482 | [6 empty] | 71826.8395 | 0.0027451 | 71826.8395 | 0.00014744 | 71826.8395 | 0.0011648
1947.179 | 0.0023204 | 1947.179 | 0.0023204 | 1947.179 | 0.0032482 | 20185.7595 | 0.0016738 | 20185.7595 | 0.00073285 | 20185.7595 | 0.0032482 | [6 empty] | 71914.8705 | 0.0028104 | 71914.8705 | 0.00015018 | 71914.8705 | 0.0011866
1947.1864 | 0.0023204 | 1947.1864 | 0.0023204 | 1947.1864 | 0.0032482 | 20942.3569 | 0.0016736 | 20942.3569 | 0.00073253 | 20942.3569 | 0.0032482 | [6 empty] | 71979.0417 | 0.0028578 | 71979.0417 | 0.00015218 | 71979.0417 | 0.0012025
1947.1912 | 0.0023204 | 1947.1912 | 0.0023204 | 1947.1912 | 0.0032482 | 21460.9355 | 0.0016735 | 21460.9355 | 0.00073231 | 21460.9355 | 0.0032482 | [6 empty] | 72004.7436 | 0.0028762 | 72004.7436 | 0.00015263 | 72004.7436 | 0.0012066
1947.196 | 0.0023204 | 1947.196 | 0.0023204 | 1947.196 | 0.0032482 | 21610.4311 | 0.0016736 | 21610.4311 | 0.00073226 | 21610.4311 | 0.0032482 | [6 empty] | 72014.4267 | 0.0028826 | 72014.4267 | 0.0001522 | 72014.4267 | 0.0012044
1947.2008 | 0.0023204 | 1947.2008 | 0.0023204 | 1947.2008 | 0.0032482 | 21653.2194 | 0.0016739 | 21653.2194 | 0.00073233 | 21653.2194 | 0.0032482 | [6 empty] | 72020.3542 | 0.0028862 | 72020.3542 | 0.0001519 | 72020.3542 | 0.0012029
1947.2057 | 0.0023204 | 1947.2057 | 0.0023204 | 1947.2057 | 0.0032482 | 21696.0077 | 0.0016743 | 21696.0077 | 0.00073237 | 21696.0077 | 0.0032482 | [6 empty] | 72026.2817 | 0.0028895 | 72026.2817 | 0.00015166 | 72026.2817 | 0.0012015
1947.2105 | 0.0023204 | 1947.2105 | 0.0023204 | 1947.2105 | 0.0032482 | 21738.796 | 0.0016748 | 21738.796 | 0.00073238 | 21738.796 | 0.0032482 | [6 empty] | 72032.5316 | 0.0028927 | 72032.5316 | 0.00015145 | 72032.5316 | 0.0012
1947.2159 | 0.0023204 | 1947.2159 | 0.0023204 | 1947.2159 | 0.0032482 | 21841.6803 | 0.0016761 | 21841.6803 | 0.00073234 | 21841.6803 | 0.0032482 | [6 empty] | 72045.3681 | 0.0028984 | 72045.3681 | 0.00015104 | 72045.3681 | 0.0011969
1947.2253 | 0.0023204 | 1947.2253 | 0.0023204 | 1947.2253 | 0.0032482 | 21987.1965 | 0.0016786 | 21987.1965 | 0.00073212 | 21987.1965 | 0.0032482 | [6 empty] | 72070.8252 | 0.0029067 | 72070.8252 | 0.00015022 | 72070.8252 | 0.0011907
1947.2299 | 0.0023204 | 1947.2299 | 0.0023204 | 1947.2299 | 0.0032482 | 22169.0624 | 0.0016823 | 22169.0624 | 0.00073162 | 22169.0624 | 0.0032482 | [6 empty] | 72112.7421 | 0.0029129 | 72112.7421 | 0.00014886 | 72112.7421 | 0.0011805
1947.2344 | 0.0023204 | 1947.2344 | 0.0023204 | 1947.2344 | 0.0032482 | 22429.9282 | 0.001689 | 22429.9282 | 0.00073048 | 22429.9282 | 0.0032482 | [6 empty] | 72178.854 | 0.002908 | 72178.854 | 0.00014672 | 72178.854 | 0.0011642
1947.2413 | 0.0023204 | 1947.2413 | 0.0023204 | 1947.2413 | 0.0032482 | 22921.256 | 0.0017052 | 22921.256 | 0.00072721 | 22921.256 | 0.0032482 | [6 empty] | 72248.1819 | 0.0028884 | 72248.1819 | 0.00014445 | 72248.1819 | 0.001147
1947.2481 | 0.0023204 | 1947.2481 | 0.0023204 | 1947.2481 | 0.0032482 | 23612.2328 | 0.0017345 | 23612.2328 | 0.00072057 | 23612.2328 | 0.0032482 | [6 empty] | 72320.1843 | 0.0028574 | 72320.1843 | 0.0001421 | 72320.1843 | 0.0011289
1947.2549 | 0.0023204 | 1947.2549 | 0.0023204 | 1947.2549 | 0.0032482 | 24166.5278 | 0.0017617 | 24166.5278 | 0.00071413 | 24166.5278 | 0.0032482 | [6 empty] | 72416.1271 | 0.0028056 | 72416.1271 | 0.00013895 | 72416.1271 | 0.0011047
1947.2617 | 0.0023204 | 1947.2617 | 0.0023204 | 1947.2617 | 0.0032482 | 24720.8229 | 0.0017922 | 24720.8229 | 0.00070674 | 24720.8229 | 0.0032482 | [6 empty] | 72558.3995 | 0.0027158 | 72558.3995 | 0.00013426 | 72558.3995 | 0.0010683
1947.2694 | 0.0023204 | 1947.2694 | 0.0023204 | 1947.2694 | 0.0032482 | 25180.4774 | 0.0018197 | 25180.4774 | 0.00070001 | 25180.4774 | 0.0032482 | [6 empty] | 72718.4002 | 0.0026042 | 72718.4002 | 0.00012897 | 72718.4002 | 0.0010271
1947.2786 | 0.0023204 | 1947.2786 | 0.0023204 | 1947.2786 | 0.0032482 | 25292.5101 | 0.0018262 | 25292.5101 | 0.00069821 | 25292.5101 | 0.0032482 | [6 empty] | 72879.2322 | 0.0024863 | 72879.2322 | 0.00012363 | 72879.2322 | 0.00098528
1947.2893 | 0.0023205 | 1947.2893 | 0.0023205 | 1947.2893 | 0.0032482 | 25404.5428 | 0.0018324 | 25404.5428 | 0.00069644 | 25404.5428 | 0.0032482 | [6 empty] | 73046.4565 | 0.002361 | 73046.4565 | 0.00011808 | 73046.4565 | 0.00094159
1947.3017 | 0.0023205 | 1947.3017 | 0.0023205 | 1947.3017 | 0.0032482 | 25516.5756 | 0.0018385 | 25516.5756 | 0.00069472 | 25516.5756 | 0.0032482 | [6 empty] | 73168.0196 | 0.0022689 | 73168.0196 | 0.00011403 | 73168.0196 | 0.0009097
1947.3166 | 0.0023205 | 1947.3166 | 0.0023205 | 1947.3166 | 0.0032482 | 25679.5955 | 0.001847 | 25679.5955 | 0.00069229 | 25679.5955 | 0.0032482 | [6 empty] | 73351.7578 | 0.0021294 | 73351.7578 | 0.0001079 | 73351.7578 | 0.00086133
1947.3354 | 0.0023205 | 1947.3354 | 0.0023205 | 1947.3354 | 0.0032482 | 25910.8905 | 0.0018588 | 25910.8905 | 0.00068898 | 25910.8905 | 0.0032482 | [6 empty] | 73503.1564 | 0.0020136 | 73503.1564 | 0.00010284 | 73503.1564 | 0.0008213
1947.3599 | 0.0023205 | 1947.3599 | 0.0023205 | 1947.3599 | 0.0032482 | 26323.0184 | 0.0018787 | 26323.0184 | 0.0006834 | 26323.0184 | 0.0032482 | [6 empty] | 73692.1564 | 0.0018689 | 73692.1564 | 9.6505e-05 | 73692.1564 | 0.00077116
1947.3927 | 0.0023205 | 1947.3927 | 0.0023205 | 1947.3927 | 0.0032482 | 27188.3926 | 0.0019173 | 27188.3926 | 0.00067274 | 27188.3926 | 0.0032482 | [6 empty] | 73898.3037 | 0.0017124 | 73898.3037 | 8.9583e-05 | 73898.3037 | 0.00071627
1947.4395 | 0.0023206 | 1947.4395 | 0.0023206 | 1947.4395 | 0.0032482 | 27834.4492 | 0.0019437 | 27834.4492 | 0.00066554 | 27834.4492 | 0.0032482 | [6 empty] | 74184.2131 | 0.0014996 | 74184.2131 | 7.9941e-05 | 74184.2131 | 0.00063975
1947.5023 | 0.0023206 | 1947.5023 | 0.0023206 | 1947.5023 | 0.0032482 | 27996.4339 | 0.0019501 | 27996.4339 | 0.00066382 | 27996.4339 | 0.0032482 | [6 empty] | 74490.7768 | 0.0012776 | 74490.7768 | 6.9539e-05 | 74490.7768 | 0.00055709
1947.5814 | 0.0023206 | 1947.5814 | 0.0023206 | 1947.5814 | 0.0032482 | 28040.2356 | 0.0019518 | 28040.2356 | 0.00066336 | 28040.2356 | 0.0032482 | [6 empty] | 74797.3406 | 0.0010649 | 74797.3406 | 5.9064e-05 | 74797.3406 | 0.00047368
1947.7087 | 0.0023207 | 1947.7087 | 0.0023207 | 1947.7087 | 0.0032482 | 28154.1184 | 0.0019562 | 28154.1184 | 0.00066216 | 28154.1184 | 0.0032482 | [6 empty] | 75103.9043 | 0.000861 | 75103.9043 | 4.8475e-05 | 75103.9043 | 0.00038925
1947.8046 | 0.0023208 | 1947.8046 | 0.0023208 | 1947.8046 | 0.0032482 | 28392.8676 | 0.0019654 | 28392.8676 | 0.00065968 | 28392.8676 | 0.0032482 | [6 empty] | 75355.3211 | 0.00069966 | 75355.3211 | 3.9693e-05 | 75355.3211 | 0.000319
1947.9004 | 0.0023208 | 1947.9004 | 0.0023208 | 1947.9004 | 0.0032482 | 28631.6168 | 0.0019744 | 28631.6168 | 0.00065725 | 28631.6168 | 0.0032482 | [6 empty] | 75512.3826 | 0.00060086 | 75512.3826 | 3.414e-05 | 75512.3826 | 0.00027454
1948.0142 | 0.0023209 | 1948.0142 | 0.0023209 | 1948.0142 | 0.0032482 | 28954.2622 | 0.0019856 | 28954.2622 | 0.00065399 | 28954.2622 | 0.0032482 | [6 empty] | 75560.5221 | 0.00057076 | 75560.5221 | 3.2428e-05 | 75560.5221 | 0.00026081
1948.1452 | 0.002321 | 1948.1452 | 0.002321 | 1948.1452 | 0.0032482 | 29276.9077 | 0.001995 | 29276.9077 | 0.00065094 | 29276.9077 | 0.0032482 | [6 empty] | 75595.9146 | 0.00054864 | 75595.9146 | 3.1166e-05 | 75595.9146 | 0.00025068
1948.2763 | 0.002321 | 1948.2763 | 0.002321 | 1948.2763 | 0.0032482 | 29608.7646 | 0.0020033 | 29608.7646 | 0.00064819 | 29608.7646 | 0.0032482 | [6 empty] | 75601.662 | 0.00054507 | 75601.662 | 3.1018e-05 | 75601.662 | 0.0002495
1948.4421 | 0.0023211 | 1948.4421 | 0.0023211 | 1948.4421 | 0.0032482 | 29940.6216 | 0.0020104 | 29940.6216 | 0.00064578 | 29940.6216 | 0.0032482 | [6 empty] | 75607.4094 | 0.00054158 | 75607.4094 | 3.1023e-05 | 75607.4094 | 0.0002495
1948.6438 | 0.0023212 | 1948.6438 | 0.0023212 | 1948.6438 | 0.0032482 | 30393.6427 | 0.0020183 | 30393.6427 | 0.00064295 | 30393.6427 | 0.0032482 | [6 empty] | 75611.5587 | 0.00053915 | 75611.5587 | 3.1049e-05 | 75611.5587 | 0.00024953
1948.8456 | 0.0023213 | 1948.8456 | 0.0023213 | 1948.8456 | 0.0032482 | 31200.1967 | 0.0020286 | 31200.1967 | 0.00063891 | 31200.1967 | 0.0032482 | [6 empty] | 75615.708 | 0.00053679 | 75615.708 | 3.1064e-05 | 75615.708 | 0.00024953
1949.0473 | 0.0023213 | 1949.0473 | 0.0023213 | 1949.0473 | 0.0032482 | 32128.1175 | 0.0020361 | 32128.1175 | 0.00063544 | 32128.1175 | 0.0032482 | [6 empty] | 75623.1211 | 0.00053275 | 75623.1211 | 3.1081e-05 | 75623.1211 | 0.00024954
1949.2512 | 0.0023214 | 1949.2512 | 0.0023214 | 1949.2512 | 0.0032482 | 32771.0123 | 0.0020408 | 32771.0123 | 0.00063348 | 32771.0123 | 0.0032482 | [6 empty] | 75638.6642 | 0.00052498 | 75638.6642 | 3.1101e-05 | 75638.6642 | 0.00024957
1949.5115 | 0.0023214 | 1949.5115 | 0.0023214 | 1949.5115 | 0.0032482 | 33413.907 | 0.0020467 | 33413.907 | 0.00063142 | 33413.907 | 0.0032482 | [6 empty] | 75675.8693 | 0.00050964 | 75675.8693 | 3.1131e-05 | 75675.8693 | 0.00024962
1949.7858 | 0.0023215 | 1949.7858 | 0.0023215 | 1949.7858 | 0.0032482 | 34104.9139 | 0.0020544 | 34104.9139 | 0.00062888 | 34104.9139 | 0.0032482 | [6 empty] | 75747.0349 | 0.00048991 | 75747.0349 | 3.1181e-05 | 75747.0349 | 0.00024975
1949.9917 | 0.0023216 | 1949.9917 | 0.0023216 | 1949.9917 | 0.0032482 | 34795.9209 | 0.0020631 | 34795.9209 | 0.00062605 | 34795.9209 | 0.0032482 | [6 empty] | 75863.4298 | 0.00047466 | 75863.4298 | 3.1258e-05 | 75863.4298 | 0.00024997
1950.1975 | 0.0023216 | 1950.1975 | 0.0023216 | 1950.1975 | 0.0032482 | 36011.5651 | 0.0020799 | 36011.5651 | 0.00062068 | 36011.5651 | 0.0032482 | [6 empty] | 76024.904 | 0.00047103 | 76024.904 | 3.1355e-05 | 76024.904 | 0.0002503
1950.3298 | 0.0023216 | 1950.3298 | 0.0023216 | 1950.3298 | 0.0032482 | 36092.1314 | 0.0020805 | 36092.1314 | 0.00062018 | 36092.1314 | 0.0032482 | [6 empty] | 76213.4885 | 0.00047644 | 76213.4885 | 3.1453e-05 | 76213.4885 | 0.00025069
1950.4978 | 0.0023217 | 1950.4978 | 0.0023217 | 1950.4978 | 0.0032482 | 36172.6977 | 0.0020808 | 36172.6977 | 0.00061974 | 36172.6977 | 0.0032482 | [6 empty] | 76414.0086 | 0.00048412 | 76414.0086 | 3.1543e-05 | 76414.0086 | 0.00025111
1950.6846 | 0.0023217 | 1950.6846 | 0.0023217 | 1950.6846 | 0.0032482 | 36253.2639 | 0.0020808 | 36253.2639 | 0.00061937 | 36253.2639 | 0.0032482 | [6 empty] | 76618.3813 | 0.00049092 | 76618.3813 | 3.1625e-05 | 76618.3813 | 0.00025154
1950.881 | 0.0023217 | 1950.881 | 0.0023217 | 1950.881 | 0.0032482 | 36373.7209 | 0.0020805 | 36373.7209 | 0.00061891 | 36373.7209 | 0.0032482 | [6 empty] | 76833.3199 | 0.00049677 | 76833.3199 | 3.1702e-05 | 76833.3199 | 0.00025199
1951.1419 | 0.0023218 | 1951.1419 | 0.0023218 | 1951.1419 | 0.0032482 | 36544.7213 | 0.0020794 | 36544.7213 | 0.00061843 | 36544.7213 | 0.0032482 | [6 empty] | 77072.4279 | 0.00050222 | 77072.4279 | 3.1782e-05 | 77072.4279 | 0.00025249
1951.4028 | 0.0023218 | 1951.4028 | 0.0023218 | 1951.4028 | 0.0032482 | 36803.2482 | 0.0020764 | 36803.2482 | 0.00061806 | 36803.2482 | 0.0032482 | [6 empty] | 77340.9431 | 0.00050736 | 77340.9431 | 3.1864e-05 | 77340.9431 | 0.00025305
1951.491 | 0.0023218 | 1951.491 | 0.0023218 | 1951.491 | 0.0032482 | 37225.6171 | 0.0020684 | 37225.6171 | 0.00061826 | 37225.6171 | 0.0032482 | [6 empty] | 77644.6066 | 0.00051214 | 77644.6066 | 3.1952e-05 | 77644.6066 | 0.00025368
1951.5996 | 0.0023218 | 1951.5996 | 0.0023218 | 1951.5996 | 0.0032482 | 37797.6847 | 0.0020525 | 37797.6847 | 0.00061982 | 37797.6847 | 0.0032482 | [6 empty] | 77990.8605 | 0.00051651 | 77990.8605 | 3.2049e-05 | 77990.8605 | 0.0002544
1951.7154 | 0.0023219 | 1951.7154 | 0.0023219 | 1951.7154 | 0.0032482 | 38386.9139 | 0.0020317 | 38386.9139 | 0.00062265 | 38386.9139 | 0.0032482 | [6 empty] | 78391.7906 | 0.00052048 | 78391.7906 | 3.2157e-05 | 78391.7906 | 0.00025523
1951.8414 | 0.0023219 | 1951.8414 | 0.0023219 | 1951.8414 | 0.0032482 | 39010.0484 | 0.0020062 | 39010.0484 | 0.00062663 | 39010.0484 | 0.0032482 | [6 empty] | 78866.6357 | 0.00052416 | 78866.6357 | 3.2283e-05 | 78866.6357 | 0.00025622
1952.0564 | 0.0023219 | 1952.0564 | 0.0023219 | 1952.0564 | 0.0032482 | 39633.1829 | 0.0019788 | 39633.1829 | 0.00063132 | 39633.1829 | 0.0032482 | [6 empty] | 79263.7563 | 0.00052619 | 79263.7563 | 3.2343e-05 | 79263.7563 | 0.00025669
1952.4288 | 0.0023219 | 1952.4288 | 0.0023219 | 1952.4288 | 0.0032482 | 39728.669 | 0.001975 | 39728.669 | 0.00063219 | 39728.669 | 0.0032482 | [6 empty] | 79431.6776 | 0.00052614 | 79431.6776 | 3.2268e-05 | 79431.6776 | 0.00025611
1952.7238 | 0.0023219 | 1952.7238 | 0.0023219 | 1952.7238 | 0.0032482 | 39824.1551 | 0.0019714 | 39824.1551 | 0.000633 | 39824.1551 | 0.0032482 | [6 empty] | 79599.5989 | 0.00052543 | 79599.5989 | 3.2194e-05 | 79599.5989 | 0.00025552
1953.0188 | 0.0023219 | 1953.0188 | 0.0023219 | 1953.0188 | 0.0032482 | 39919.6412 | 0.001968 | 39919.6412 | 0.00063377 | 39919.6412 | 0.0032482 | [6 empty] | 79767.5202 | 0.00052442 | 79767.5202 | 3.2121e-05 | 79767.5202 | 0.00025494
1953.3138 | 0.0023219 | 1953.3138 | 0.0023219 | 1953.3138 | 0.0032482 | 40107.617 | 0.0019618 | 40107.617 | 0.00063516 | 40107.617 | 0.0032482 | [6 empty] | 80511.0529 | 0.00051958 | 80511.0529 | 3.1795e-05 | 80511.0529 | 0.00025237
1953.6087 | 0.0023219 | 1953.6087 | 0.0023219 | 1953.6087 | 0.0032482 | 40414.962 | 0.0019529 | 40414.962 | 0.00063713 | 40414.962 | 0.0032482 | [6 empty] | 81863.1709 | 0.00051033 | 81863.1709 | 3.1204e-05 | 81863.1709 | 0.00024768
1954.0179 | 0.0023219 | 1954.0179 | 0.0023219 | 1954.0179 | 0.0032482 | 40938.9844 | 0.0019404 | 40938.9844 | 0.0006398 | 40938.9844 | 0.0032482 | [6 empty] | 83429.626 | 0.00049961 | 83429.626 | 3.0519e-05 | 83429.626 | 0.00024224
1954.3873 | 0.0023219 | 1954.3873 | 0.0023219 | 1954.3873 | 0.0032482 | 41639.0824 | 0.0019279 | 41639.0824 | 0.00064226 | 41639.0824 | 0.0032482 | [6 empty] | 85157.626 | 0.00048786 | 85157.626 | 2.9761e-05 | 85157.626 | 0.00023622
1954.7566 | 0.0023219 | 1954.7566 | 0.0023219 | 1954.7566 | 0.0032482 | 42369.2633 | 0.0019187 | 42369.2633 | 0.00064384 | 42369.2633 | 0.0032482 | [6 empty] | 86400 | 0.00047938 | 86400 | 2.9215e-05 | 86400 | 0.00023189
1955.126 | 0.0023219 | 1955.126 | 0.0023219 | 1955.126 | 0.0032482 | 43114.8587 | 0.0019121 | 43114.8587 | 0.00064471 | 43114.8587 | 0.0032482
1955.4953 | 0.0023219 | 1955.4953 | 0.0023219 | 1955.4953 | 0.0032482 | 43182.2423 | 0.0019116 | 43182.2423 | 0.00064476 | 43182.2423 | 0.0032482
1955.8789 | 0.0023219 | 1955.8789 | 0.0023219 | 1955.8789 | 0.0032482 | 43220.7483 | 0.0019114 | 43220.7483 | 0.00064478 | 43220.7483 | 0.0032482
1956.4852 | 0.0023219 | 1956.4852 | 0.0023219 | 1956.4852 | 0.0032482 | 43292.2979 | 0.0019109 | 43292.2979 | 0.00064483 | 43292.2979 | 0.0032482
1956.9052 | 0.0023219 | 1956.9052 | 0.0023219 | 1956.9052 | 0.0032482 | 43515.6559 | 0.0019095 | 43515.6559 | 0.00064495 | 43515.6559 | 0.0032482
1957.3251 | 0.0023219 | 1957.3251 | 0.0023219 | 1957.3251 | 0.0032482 | 44053.9863 | 0.0019065 | 44053.9863 | 0.0006451 | 44053.9863 | 0.0032482
1957.745 | 0.0023219 | 1957.745 | 0.0023219 | 1957.745 | 0.0032482 | 44871.3176 | 0.0019031 | 44871.3176 | 0.00064505 | 44871.3176 | 0.0032482
1958.1973 | 0.0023219 | 1958.1973 | 0.0023219 | 1958.1973 | 0.0032482 | 46118.5648 | 0.0018996 | 46118.5648 | 0.00064456 | 46118.5648 | 0.0032482
1958.7735 | 0.0023219 | 1958.7735 | 0.0023219 | 1958.7735 | 0.0032482 | 47624.8874 | 0.0018969 | 47624.8874 | 0.00064355 | 47624.8874 | 0.0032482
1959.2473 | 0.0023219 | 1959.2473 | 0.0023219 | 1959.2473 | 0.0032482 | 49259.4644 | 0.001895 | 49259.4644 | 0.0006422 | 49259.4644 | 0.0032482
1959.7211 | 0.0023219 | 1959.7211 | 0.0023219 | 1959.7211 | 0.0032482 | 50894.0413 | 0.0018936 | 50894.0413 | 0.00064074 | 50894.0413 | 0.0032482
1960.1984 | 0.0023219 | 1960.1984 | 0.0023219 | 1960.1984 | 0.0032482 | 52622.0413 | 0.0018922 | 52622.0413 | 0.00063918 | 52622.0413 | 0.0032482
1960.8304 | 0.0023219 | 1960.8304 | 0.0023219 | 1960.8304 | 0.0032482 | 54350.0413 | 0.001891 | 54350.0413 | 0.00063761 | 54350.0413 | 0.0032482
1961.4391 | 0.0023219 | 1961.4391 | 0.0023219 | 1961.4391 | 0.0032482 | 56078.0413 | 0.0018897 | 56078.0413 | 0.00063605 | 56078.0413 | 0.0032482
1962.0477 | 0.0023218 | 1962.0477 | 0.0023218 | 1962.0477 | 0.0032482 | 57054.7082 | 0.001889 | 57054.7082 | 0.00063517 | 57054.7082 | 0.0032482
1962.6563 | 0.0023218 | 1962.6563 | 0.0023218 | 1962.6563 | 0.0032482 | 57479.2662 | 0.0018887 | 57479.2662 | 0.00063479 | 57479.2662 | 0.0032482
1963.44 | 0.0023218 | 1963.44 | 0.0023218 | 1963.44 | 0.0032482 | 57655.8688 | 0.0018892 | 57655.8688 | 0.00063471 | 57655.8688 | 0.0032482
1964.2969 | 0.0023218 | 1964.2969 | 0.0023218 | 1964.2969 | 0.0032482 | 57802.7146 | 0.0018908 | 57802.7146 | 0.00063473 | 57802.7146 | 0.0032482
1965.1537 | 0.0023218 | 1965.1537 | 0.0023218 | 1965.1537 | 0.0032482 | 57910.117 | 0.0018924 | 57910.117 | 0.00063462 | 57910.117 | 0.0032482
1966.0124 | 0.0023218 | 1966.0124 | 0.0023218 | 1966.0124 | 0.0032482 | 58017.5194 | 0.0018944 | 58017.5194 | 0.00063441 | 58017.5194 | 0.0032482
1966.9745 | 0.0023218 | 1966.9745 | 0.0023218 | 1966.9745 | 0.0032482 | 58172.5397 | 0.0018979 | 58172.5397 | 0.00063397 | 58172.5397 | 0.0032482
1967.9367 | 0.0023218 | 1967.9367 | 0.0023218 | 1967.9367 | 0.0032482 | 58359.4118 | 0.0019028 | 58359.4118 | 0.00063322 | 58359.4118 | 0.0032482
1969.0449 | 0.0023218 | 1969.0449 | 0.0023218 | 1969.0449 | 0.0032482 | 58426.8344 | 0.0019049 | 58426.8344 | 0.0006329 | 58426.8344 | 0.0032482
1970.3804 | 0.0023218 | 1970.3804 | 0.0023218 | 1970.3804 | 0.0032482 | 58616.8276 | 0.001911 | 58616.8276 | 0.00063183 | 58616.8276 | 0.0032482
1971.7159 | 0.0023218 | 1971.7159 | 0.0023218 | 1971.7159 | 0.0032482 | 59054.1841 | 0.0019281 | 59054.1841 | 0.00062867 | 59054.1841 | 0.0032482
1973.6702 | 0.0023218 | 1973.6702 | 0.0023218 | 1973.6702 | 0.0032482 | 59491.5407 | 0.0019486 | 59491.5407 | 0.00062461 | 59491.5407 | 0.0032482
1975.6244 | 0.0023218 | 1975.6244 | 0.0023218 | 1975.6244 | 0.0032482 | 60019.8305 | 0.0019773 | 60019.8305 | 0.00061872 | 60019.8305 | 0.0032482
1978.2979 | 0.0023218 | 1978.2979 | 0.0023218 | 1978.2979 | 0.0032482 | 60688.2381 | 0.0020189 | 60688.2381 | 0.00061002 | 60688.2381 | 0.0032482
1981.1316 | 0.0023218 | 1981.1316 | 0.0023218 | 1981.1316 | 0.0032482 | 61129.598 | 0.0020493 | 61129.598 | 0.00060363 | 61129.598 | 0.0032482
1986.1144 | 0.0023217 | 1986.1144 | 0.0023217 | 1986.1144 | 0.0032482 | 61268.0352 | 0.0020586 | 61268.0352 | 0.00060142 | 61268.0352 | 0.0032482
1991.8083 | 0.0023217 | 1991.8083 | 0.0023217 | 1991.8083 | 0.0032482 | 61406.4723 | 0.002067 | 61406.4723 | 0.00059916 | 61406.4723 | 0.0032482
2006.1606 | 0.0023216 | 2006.1606 | 0.0023216 | 2006.1606 | 0.0032482 | 61542.0563 | 0.0020746 | 61542.0563 | 0.00059708 | 61542.0563 | 0.0032482
2023.4701 | 0.0023215 | 2023.4701 | 0.0023215 | 2023.4701 | 0.0032482 | 61677.6402 | 0.0020817 | 61677.6402 | 0.00059513 | 61677.6402 | 0.0032482
2043.3094 | 0.0023214 | 2043.3094 | 0.0023214 | 2043.3094 | 0.0032482 | 61838.4716 | 0.0020896 | 61838.4716 | 0.00059296 | 61838.4716 | 0.0032482
2066.8932 | 0.0023213 | 2066.8932 | 0.0023213 | 2066.8932 | 0.0032482 | 62117.6406 | 0.002102 | 62117.6406 | 0.00058951 | 62117.6406 | 0.0032482
2098.3246 | 0.0023211 | 2098.3246 | 0.0023211 | 2098.3246 | 0.0032482 | 62707.8536 | 0.0021235 | 62707.8536 | 0.00058339 | 62707.8536 | 0.0032482
2144.3038 | 0.0023209 | 2144.3038 | 0.0023209 | 2144.3038 | 0.0032482 | 63441.2436 | 0.002143 | 63441.2436 | 0.00057755 | 63441.2436 | 0.0032482
2185.7666 | 0.0023207 | 2185.7666 | 0.0023207 | 2185.7666 | 0.0032482 | 64194.901 | 0.0021566 | 64194.901 | 0.00057308 | 64194.901 | 0.0032482
2197.461 | 0.0023206 | 2197.461 | 0.0023206 | 2197.461 | 0.0032482 | 64948.5584 | 0.0021656 | 64948.5584 | 0.00056972 | 64948.5584 | 0.0032482
2240.553 | 0.0023204 | 2240.553 | 0.0023204 | 2240.553 | 0.0032482 | 65745.1122 | 0.0021717 | 65745.1122 | 0.00056696 | 65745.1122 | 0.0032482
2333.837 | 0.00232 | 2333.837 | 0.00232 | 2333.837 | 0.0032482 | 66644.0146 | 0.0021757 | 66644.0146 | 0.00056452 | 66644.0146 | 0.0032482
2434.2602 | 0.0023195 | 2434.2602 | 0.0023195 | 2434.2602 | 0.0032482 | 67542.9169 | 0.0021777 | 67542.9169 | 0.00056256 | 67542.9169 | 0.0032482
2534.6834 | 0.002319 | 2534.6834 | 0.002319 | 2534.6834 | 0.0032482 | 68699.5224 | 0.0021785 | 68699.5224 | 0.00056046 | 68699.5224 | 0.0032482
2635.1066 | 0.0023185 | 2635.1066 | 0.0023185 | 2635.1066 | 0.0032482 | 70131.6501 | 0.0021779 | 70131.6501 | 0.00055824 | 70131.6501 | 0.0032482
2744.7581 | 0.002318 | 2744.7581 | 0.002318 | 2744.7581 | 0.0032482 | 71836.4912 | 0.002176 | 71836.4912 | 0.0005559 | 71836.4912 | 0.0032482
2755.9542 | 0.002318 | 2755.9542 | 0.002318 | 2755.9542 | 0.0032482 | 73564.4912 | 0.0021734 | 73564.4912 | 0.0005537 | 73564.4912 | 0.0032482
2812.611 | 0.0023177 | 2812.611 | 0.0023177 | 2812.611 | 0.0032482 | 75292.4912 | 0.0021705 | 75292.4912 | 0.00055157 | 75292.4912 | 0.0032482
2966.7199 | 0.002317 | 2966.7199 | 0.002317 | 2966.7199 | 0.0032482 | 77020.4912 | 0.0021676 | 77020.4912 | 0.0005495 | 77020.4912 | 0.0032482
3287.1807 | 0.0023155 | 3287.1807 | 0.0023155 | 3287.1807 | 0.0032482 | 78748.4912 | 0.0021647 | 78748.4912 | 0.00054745 | 78748.4912 | 0.0032482
3721.2648 | 0.0023129 | 3721.2648 | 0.0023129 | 3721.2648 | 0.0032482 | 79200.7534 | 0.002164 | 79200.7534 | 0.00054692 | 79200.7534 | 0.0032482
3910.3518 | 0.0023112 | 3910.3518 | 0.0023112 | 3910.3518 | 0.0032482 | 79301.9522 | 0.0021632 | 79301.9522 | 0.00054664 | 79301.9522 | 0.0032482
3997.1639 | 0.0023105 | 3997.1639 | 0.0023105 | 3997.1639 | 0.0032482 | 79403.1509 | 0.0021621 | 79403.1509 | 0.00054646 | 79403.1509 | 0.0032482
4020.4465 | 0.0023103 | 4020.4465 | 0.0023103 | 4020.4465 | 0.0032482 | 79504.3496 | 0.0021606 | 79504.3496 | 0.00054634 | 79504.3496 | 0.0032482
4030.7988 | 0.0023102 | 4030.7988 | 0.0023102 | 4030.7988 | 0.0032482 | 79636.6097 | 0.0021583 | 79636.6097 | 0.00054628 | 79636.6097 | 0.0032482
4095.2572 | 0.0023096 | 4095.2572 | 0.0023096 | 4095.2572 | 0.0032482 | 79827.23 | 0.0021543 | 79827.23 | 0.00054635 | 79827.23 | 0.0032482
4290.6349 | 0.0023078 | 4290.6349 | 0.0023078 | 4290.6349 | 0.0032482 | 80204.3697 | 0.0021442 | 80204.3697 | 0.00054699 | 80204.3697 | 0.0032482
4650.7689 | 0.0023047 | 4650.7689 | 0.0023047 | 4650.7689 | 0.0032482 | 80790.8891 | 0.0021238 | 80790.8891 | 0.00054908 | 80790.8891 | 0.0032482
5253.4783 | 0.0022994 | 5253.4783 | 0.0022994 | 5253.4783 | 0.0032482 | 81411.7323 | 0.0020975 | 81411.7323 | 0.00055243 | 81411.7323 | 0.0032482
5471.4591 | 0.0022975 | 5471.4591 | 0.0022975 | 5471.4591 | 0.0032482 | 82032.5756 | 0.0020679 | 82032.5756 | 0.00055662 | 82032.5756 | 0.0032482
5528.6009 | 0.002297 | 5528.6009 | 0.002297 | 5528.6009 | 0.0032482 | 82696.5335 | 0.0020339 | 82696.5335 | 0.00056174 | 82696.5335 | 0.0032482
5542.1793 | 0.0022969 | 5542.1793 | 0.0022969 | 5542.1793 | 0.0032482 | 83430.036 | 0.001995 | 83430.036 | 0.00056789 | 83430.036 | 0.0032482
5601.327 | 0.0022964 | 5601.327 | 0.0022964 | 5601.327 | 0.0032482 | 84163.5384 | 0.0019554 | 84163.5384 | 0.00057436 | 84163.5384 | 0.0032482
6024.7928 | 0.0022928 | 6024.7928 | 0.0022928 | 6024.7928 | 0.0032482 | 85040.0225 | 0.0019083 | 85040.0225 | 0.0005823 | 85040.0225 | 0.0032482
7014.507 | 0.0022846 | 7014.507 | 0.0022846 | 7014.507 | 0.0032482 | 86092.8151 | 0.0018528 | 86092.8151 | 0.00059197 | 86092.8151 | 0.0032482
7376.6234 | 0.0022824 | 7376.6234 | 0.0022824 | 7376.6234 | 0.0032482 | 86400 | 0.001837 | 86400 | 0.0005948 | 86400 | 0.0032482
7738.7399 | 0.002281 | 7738.7399 | 0.002281 | 7738.7399 | 0.0032482
8052.0392 | 0.0022797 | 8052.0392 | 0.0022797 | 8052.0392 | 0.0032482
8365.3386 | 0.0022785 | 8365.3386 | 0.0022785 | 8365.3386 | 0.0032482
9033.7409 | 0.0022759 | 9033.7409 | 0.0022759 | 9033.7409 | 0.0032482
10534.7587 | 0.0022701 | 10534.7587 | 0.0022701 | 10534.7587 | 0.0032482
12262.7587 | 0.0022633 | 12262.7587 | 0.0022633 | 12262.7587 | 0.0032482
13990.7587 | 0.0022565 | 13990.7587 | 0.0022565 | 13990.7587 | 0.0032482
14787.3489 | 0.002254 | 14787.3489 | 0.002254 | 14787.3489 | 0.0032482
15583.9392 | 0.002252 | 15583.9392 | 0.002252 | 15583.9392 | 0.0032482
16384.6119 | 0.00225 | 16384.6119 | 0.00225 | 16384.6119 | 0.0032482
17185.2847 | 0.0022479 | 17185.2847 | 0.0022479 | 17185.2847 | 0.0032482
17683.0965 | 0.0022467 | 17683.0965 | 0.0022467 | 17683.0965 | 0.0032482
17919.7542 | 0.002246 | 17919.7542 | 0.002246 | 17919.7542 | 0.0032482
18018.969 | 0.0022462 | 18018.969 | 0.0022462 | 18018.969 | 0.0032482
18060.8395 | 0.002247 | 18060.8395 | 0.002247 | 18060.8395 | 0.0032482
18102.71 | 0.0022478 | 18102.71 | 0.0022478 | 18102.71 | 0.0032482
18144.5805 | 0.0022485 | 18144.5805 | 0.0022485 | 18144.5805 | 0.0032482
18227.8245 | 0.0022501 | 18227.8245 | 0.0022501 | 18227.8245 | 0.0032482
18409.0802 | 0.0022534 | 18409.0802 | 0.0022534 | 18409.0802 | 0.0032482
18710.1123 | 0.0022589 | 18710.1123 | 0.0022589 | 18710.1123 | 0.0032482
19074.5068 | 0.0022655 | 19074.5068 | 0.0022655 | 19074.5068 | 0.0032482
19452.2365 | 0.0022721 | 19452.2365 | 0.0022721 | 19452.2365 | 0.0032482
19829.9662 | 0.0022787 | 19829.9662 | 0.0022787 | 19829.9662 | 0.0032482
20590.0411 | 0.0022914 | 20590.0411 | 0.0022914 | 20590.0411 | 0.0032482
21350.1161 | 0.0023035 | 21350.1161 | 0.0023035 | 21350.1161 | 0.0032482
21593.2477 | 0.0023073 | 21593.2477 | 0.0023073 | 21593.2477 | 0.0032482
21650.6472 | 0.0023075 | 21650.6472 | 0.0023075 | 21650.6472 | 0.0032482
21708.0467 | 0.0023076 | 21708.0467 | 0.0023076 | 21708.0467 | 0.0032482
21765.4463 | 0.0023078 | 21765.4463 | 0.0023078 | 21765.4463 | 0.0032482
21860.3395 | 0.002308 | 21860.3395 | 0.002308 | 21860.3395 | 0.0032482
22191.2471 | 0.0023087 | 22191.2471 | 0.0023087 | 22191.2471 | 0.0032482
22957.3504 | 0.00231 | 22957.3504 | 0.00231 | 22957.3504 | 0.0032482
24056.1515 | 0.0023115 | 24056.1515 | 0.0023115 | 24056.1515 | 0.0032482
24917.1927 | 0.0023121 | 24917.1927 | 0.0023121 | 24917.1927 | 0.0032482
25288.2535 | 0.0023117 | 25288.2535 | 0.0023117 | 25288.2535 | 0.0032482
25494.9727 | 0.0023103 | 25494.9727 | 0.0023103 | 25494.9727 | 0.0032482
25658.2818 | 0.0023091 | 25658.2818 | 0.0023091 | 25658.2818 | 0.0032482
25821.5908 | 0.002308 | 25821.5908 | 0.002308 | 25821.5908 | 0.0032482
26123.4069 | 0.002306 | 26123.4069 | 0.002306 | 26123.4069 | 0.0032482
27039.1165 | 0.0022996 | 27039.1165 | 0.0022996 | 27039.1165 | 0.0032482
27181.9425 | 0.0022986 | 27181.9425 | 0.0022986 | 27181.9425 | 0.0032482
27193.2546 | 0.0022985 | 27193.2546 | 0.0022985 | 27193.2546 | 0.0032482
27197.3274 | 0.0022985 | 27197.3274 | 0.0022985 | 27197.3274 | 0.0032482
27214.7681 | 0.0022984 | 27214.7681 | 0.0022984 | 27214.7681 | 0.0032482
27245.1449 | 0.0022982 | 27245.1449 | 0.0022982 | 27245.1449 | 0.0032482
27351.5557 | 0.0022974 | 27351.5557 | 0.0022974 | 27351.5557 | 0.0032482
27651.9141 | 0.0022953 | 27651.9141 | 0.0022953 | 27651.9141 | 0.0032482
28792.3941 | 0.0022872 | 28792.3941 | 0.0022872 | 28792.3941 | 0.0032482
29071.4429 | 0.0022844 | 29071.4429 | 0.0022844 | 29071.4429 | 0.0032482
29350.4917 | 0.0022816 | 29350.4917 | 0.0022816 | 29350.4917 | 0.0032482
29534.6639 | 0.0022798 | 29534.6639 | 0.0022798 | 29534.6639 | 0.0032482
29543.8344 | 0.0022797 | 29543.8344 | 0.0022797 | 29543.8344 | 0.0032482
29548.837 | 0.0022797 | 29548.837 | 0.0022797 | 29548.837 | 0.0032482
29572.0801 | 0.0022794 | 29572.0801 | 0.0022794 | 29572.0801 | 0.0032482
29613.9525 | 0.002279 | 29613.9525 | 0.002279 | 29613.9525 | 0.0032482
29651.1769 | 0.0022786 | 29651.1769 | 0.0022786 | 29651.1769 | 0.0032482
29661.9551 | 0.0022785 | 29661.9551 | 0.0022785 | 29661.9551 | 0.0032482
29769.737 | 0.0022775 | 29769.737 | 0.0022775 | 29769.737 | 0.0032482
30179.7802 | 0.0022734 | 30179.7802 | 0.0022734 | 30179.7802 | 0.0032482
31474.5677 | 0.0022606 | 31474.5677 | 0.0022606 | 31474.5677 | 0.0032482
32740.345 | 0.0022488 | 32740.345 | 0.0022488 | 32740.345 | 0.0032482
33770.2591 | 0.0022404 | 33770.2591 | 0.0022404 | 33770.2591 | 0.0032482
33780.9197 | 0.0022403 | 33780.9197 | 0.0022403 | 33780.9197 | 0.0032482
33783.4818 | 0.0022403 | 33783.4818 | 0.0022403 | 33783.4818 | 0.0032482
33795.9291 | 0.0022402 | 33795.9291 | 0.0022402 | 33795.9291 | 0.0032482
33818.9089 | 0.00224 | 33818.9089 | 0.00224 | 33818.9089 | 0.0032482
33837.4255 | 0.0022398 | 33837.4255 | 0.0022398 | 33837.4255 | 0.0032482
33840.598 | 0.0022398 | 33840.598 | 0.0022398 | 33840.598 | 0.0032482
33852.7566 | 0.0022397 | 33852.7566 | 0.0022397 | 33852.7566 | 0.0032482
33872.885 | 0.0022395 | 33872.885 | 0.0022395 | 33872.885 | 0.0032482
33878.3429 | 0.0022395 | 33878.3429 | 0.0022395 | 33878.3429 | 0.0032482
33898.068 | 0.0022393 | 33898.068 | 0.0022393 | 33898.068 | 0.0032482
33918.789 | 0.0022392 | 33918.789 | 0.0022392 | 33918.789 | 0.0032482
33921.8955 | 0.0022391 | 33921.8955 | 0.0022391 | 33921.8955 | 0.0032482
33936.4256 | 0.002239 | 33936.4256 | 0.002239 | 33936.4256 | 0.0032482
33962.6969 | 0.0022388 | 33962.6969 | 0.0022388 | 33962.6969 | 0.0032482
33986.233 | 0.0022386 | 33986.233 | 0.0022386 | 33986.233 | 0.0032482
33989.2289 | 0.0022386 | 33989.2289 | 0.0022386 | 33989.2289 | 0.0032482
34004.4267 | 0.0022385 | 34004.4267 | 0.0022385 | 34004.4267 | 0.0032482
34023.1366 | 0.0022383 | 34023.1366 | 0.0022383 | 34023.1366 | 0.0032482
34037.0869 | 0.0022382 | 34037.0869 | 0.0022382 | 34037.0869 | 0.0032482
34039.7825 | 0.0022382 | 34039.7825 | 0.0022382 | 34039.7825 | 0.0032482
34053.663 | 0.002238 | 34053.663 | 0.002238 | 34053.663 | 0.0032482
34070.9388 | 0.0022379 | 34070.9388 | 0.0022379 | 34070.9388 | 0.0032482
34083.7796 | 0.0022378 | 34083.7796 | 0.0022378 | 34083.7796 | 0.0032482
34086.2152 | 0.0022378 | 34086.2152 | 0.0022378 | 34086.2152 | 0.0032482
34098.6961 | 0.0022377 | 34098.6961 | 0.0022377 | 34098.6961 | 0.0032482
34114.1902 | 0.0022376 | 34114.1902 | 0.0022376 | 34114.1902 | 0.0032482
34131.6395 | 0.0022374 | 34131.6395 | 0.0022374 | 34131.6395 | 0.0032482
34134.365 | 0.0022374 | 34134.365 | 0.0022374 | 34134.365 | 0.0032482
34145.9216 | 0.0022373 | 34145.9216 | 0.0022373 | 34145.9216 | 0.0032482
34154.6583 | 0.0022372 | 34154.6583 | 0.0022372 | 34154.6583 | 0.0032482
34157.0284 | 0.0022372 | 34157.0284 | 0.0022372 | 34157.0284 | 0.0032482
34166.5636 | 0.0022371 | 34166.5636 | 0.0022371 | 34166.5636 | 0.0032482
34182.7832 | 0.002237 | 34182.7832 | 0.002237 | 34182.7832 | 0.0032482
34205.6468 | 0.0022368 | 34205.6468 | 0.0022368 | 34205.6468 | 0.0032482
34380.241 | 0.0022354 | 34380.241 | 0.0022354 | 34380.241 | 0.0032482
34913.3858 | 0.002231 | 34913.3858 | 0.002231 | 34913.3858 | 0.0032482
35500.1232 | 0.0022262 | 35500.1232 | 0.0022262 | 35500.1232 | 0.0032482
35871.0073 | 0.0022232 | 35871.0073 | 0.0022232 | 35871.0073 | 0.0032482
36008.9146 | 0.0022218 | 36008.9146 | 0.0022218 | 36008.9146 | 0.0032482
36048.1899 | 0.0022207 | 36048.1899 | 0.0022207 | 36048.1899 | 0.0032482
36087.4653 | 0.0022196 | 36087.4653 | 0.0022196 | 36087.4653 | 0.0032482
36126.7406 | 0.0022185 | 36126.7406 | 0.0022185 | 36126.7406 | 0.0032482
36192.5825 | 0.0022166 | 36192.5825 | 0.0022166 | 36192.5825 | 0.0032482
36327.5569 | 0.0022128 | 36327.5569 | 0.0022128 | 36327.5569 | 0.0032482
36627.6221 | 0.0022044 | 36627.6221 | 0.0022044 | 36627.6221 | 0.0032482
37257.5654 | 0.0021875 | 37257.5654 | 0.0021875 | 37257.5654 | 0.0032482
37434.4406 | 0.0021829 | 37434.4406 | 0.0021829 | 37434.4406 | 0.0032482
37440.5813 | 0.0021827 | 37440.5813 | 0.0021827 | 37440.5813 | 0.0032482
37443.9312 | 0.0021826 | 37443.9312 | 0.0021826 | 37443.9312 | 0.0032482
37460.872 | 0.0021822 | 37460.872 | 0.0021822 | 37460.872 | 0.0032482
37469.9626 | 0.002182 | 37469.9626 | 0.002182 | 37469.9626 | 0.0032482
37497.6557 | 0.0021812 | 37497.6557 | 0.0021812 | 37497.6557 | 0.0032482
37500.7296 | 0.0021812 | 37500.7296 | 0.0021812 | 37500.7296 | 0.0032482
37513.0322 | 0.0021808 | 37513.0322 | 0.0021808 | 37513.0322 | 0.0032482
37522.1107 | 0.0021806 | 37522.1107 | 0.0021806 | 37522.1107 | 0.0032482
37591.5158 | 0.0021788 | 37591.5158 | 0.0021788 | 37591.5158 | 0.0032482
37824.3061 | 0.002173 | 37824.3061 | 0.002173 | 37824.3061 | 0.0032482
38421.9514 | 0.0021584 | 38421.9514 | 0.0021584 | 38421.9514 | 0.0032482
39532.6642 | 0.0021334 | 39532.6642 | 0.0021334 | 39532.6642 | 0.0032482
39640.5324 | 0.0021317 | 39640.5324 | 0.0021317 | 39640.5324 | 0.0032482
39748.4006 | 0.0021308 | 39748.4006 | 0.0021308 | 39748.4006 | 0.0032482
39826.4019 | 0.0021303 | 39826.4019 | 0.0021303 | 39826.4019 | 0.0032482
39904.4032 | 0.0021297 | 39904.4032 | 0.0021297 | 39904.4032 | 0.0032482
40012.5288 | 0.0021288 | 40012.5288 | 0.0021288 | 40012.5288 | 0.0032482
40222.2338 | 0.0021273 | 40222.2338 | 0.0021273 | 40222.2338 | 0.0032482
40924.1831 | 0.002122 | 40924.1831 | 0.002122 | 40924.1831 | 0.0032482
42261.2936 | 0.0021124 | 42261.2936 | 0.0021124 | 42261.2936 | 0.0032482
43296.4799 | 0.0021054 | 43296.4799 | 0.0021054 | 43296.4799 | 0.0032482
43528.487 | 0.0021043 | 43528.487 | 0.0021043 | 43528.487 | 0.0032482
43572.5097 | 0.0021041 | 43572.5097 | 0.0021041 | 43572.5097 | 0.0032482
43579.3506 | 0.0021041 | 43579.3506 | 0.0021041 | 43579.3506 | 0.0032482
43582.5011 | 0.0021041 | 43582.5011 | 0.0021041 | 43582.5011 | 0.0032482
43597.2423 | 0.002104 | 43597.2423 | 0.002104 | 43597.2423 | 0.0032482
43631.3073 | 0.0021038 | 43631.3073 | 0.0021038 | 43631.3073 | 0.0032482
43689.5359 | 0.0021036 | 43689.5359 | 0.0021036 | 43689.5359 | 0.0032482
43794.3276 | 0.0021031 | 43794.3276 | 0.0021031 | 43794.3276 | 0.0032482
43971.9076 | 0.0021022 | 43971.9076 | 0.0021022 | 43971.9076 | 0.0032482
44250.006 | 0.0021009 | 44250.006 | 0.0021009 | 44250.006 | 0.0032482
44409.7751 | 0.0021002 | 44409.7751 | 0.0021002 | 44409.7751 | 0.0032482
44457.3165 | 0.0021 | 44457.3165 | 0.0021 | 44457.3165 | 0.0032482
44460.5644 | 0.0020999 | 44460.5644 | 0.0020999 | 44460.5644 | 0.0032482
44470.9567 | 0.0020999 | 44470.9567 | 0.0020999 | 44470.9567 | 0.0032482
44481.4986 | 0.0020998 | 44481.4986 | 0.0020998 | 44481.4986 | 0.0032482
44485.0565 | 0.0020998 | 44485.0565 | 0.0020998 | 44485.0565 | 0.0032482
44497.0369 | 0.0020998 | 44497.0369 | 0.0020998 | 44497.0369 | 0.0032482
44505.3131 | 0.0020997 | 44505.3131 | 0.0020997 | 44505.3131 | 0.0032482
44569.5025 | 0.0020994 | 44569.5025 | 0.0020994 | 44569.5025 | 0.0032482
44753.8436 | 0.0020986 | 44753.8436 | 0.0020986 | 44753.8436 | 0.0032482
45171.1819 | 0.0020966 | 45171.1819 | 0.0020966 | 45171.1819 | 0.0032482
45948.364 | 0.002093 | 45948.364 | 0.002093 | 45948.364 | 0.0032482
47380.2462 | 0.0020859 | 47380.2462 | 0.0020859 | 47380.2462 | 0.0032482
48812.1284 | 0.0020783 | 48812.1284 | 0.0020783 | 48812.1284 | 0.0032482
49947.8652 | 0.0020724 | 49947.8652 | 0.0020724 | 49947.8652 | 0.0032482
50588.1287 | 0.0020696 | 50588.1287 | 0.0020696 | 50588.1287 | 0.0032482
50985.9923 | 0.0020684 | 50985.9923 | 0.0020684 | 50985.9923 | 0.0032482
51294.6627 | 0.0020676 | 51294.6627 | 0.0020676 | 51294.6627 | 0.0032482
51603.3331 | 0.0020666 | 51603.3331 | 0.0020666 | 51603.3331 | 0.0032482
52121.2143 | 0.0020651 | 52121.2143 | 0.0020651 | 52121.2143 | 0.0032482
53455.3068 | 0.002061 | 53455.3068 | 0.002061 | 53455.3068 | 0.0032482
54266.4433 | 0.0020581 | 54266.4433 | 0.0020581 | 54266.4433 | 0.0032482
55077.5799 | 0.0020546 | 55077.5799 | 0.0020546 | 55077.5799 | 0.0032482
55696.2857 | 0.0020519 | 55696.2857 | 0.0020519 | 55696.2857 | 0.0032482
56314.9915 | 0.0020492 | 56314.9915 | 0.0020492 | 56314.9915 | 0.0032482
57395.1092 | 0.0020444 | 57395.1092 | 0.0020444 | 57395.1092 | 0.0032482
59123.1092 | 0.002037 | 59123.1092 | 0.002037 | 59123.1092 | 0.0032482
60851.1092 | 0.0020296 | 60851.1092 | 0.0020296 | 60851.1092 | 0.0032482
61526.4157 | 0.0020266 | 61526.4157 | 0.0020266 | 61526.4157 | 0.0032482
62201.7221 | 0.0020239 | 62201.7221 | 0.0020239 | 62201.7221 | 0.0032482
62818.5702 | 0.0020214 | 62818.5702 | 0.0020214 | 62818.5702 | 0.0032482
63435.4184 | 0.0020189 | 63435.4184 | 0.0020189 | 63435.4184 | 0.0032482
64110.1078 | 0.0020161 | 64110.1078 | 0.0020161 | 64110.1078 | 0.0032482
64505.6861 | 0.0020144 | 64505.6861 | 0.0020144 | 64505.6861 | 0.0032482
64718.611 | 0.0020135 | 64718.611 | 0.0020135 | 64718.611 | 0.0032482
64806.9755 | 0.0020133 | 64806.9755 | 0.0020133 | 64806.9755 | 0.0032482
64819.5624 | 0.0020135 | 64819.5624 | 0.0020135 | 64819.5624 | 0.0032482
64826.4755 | 0.0020136 | 64826.4755 | 0.0020136 | 64826.4755 | 0.0032482
64832.1266 | 0.0020137 | 64832.1266 | 0.0020137 | 64832.1266 | 0.0032482
64837.7777 | 0.0020138 | 64837.7777 | 0.0020138 | 64837.7777 | 0.0032482
64843.9548 | 0.0020139 | 64843.9548 | 0.0020139 | 64843.9548 | 0.0032482
64860.1072 | 0.0020142 | 64860.1072 | 0.0020142 | 64860.1072 | 0.0032482
64876.2596 | 0.0020145 | 64876.2596 | 0.0020145 | 64876.2596 | 0.0032482
64916.7911 | 0.0020153 | 64916.7911 | 0.0020153 | 64916.7911 | 0.0032482
64960.4066 | 0.0020163 | 64960.4066 | 0.0020163 | 64960.4066 | 0.0032482
64964.4085 | 0.0020164 | 64964.4085 | 0.0020164 | 64964.4085 | 0.0032482
64968.3958 | 0.0020166 | 64968.3958 | 0.0020166 | 64968.3958 | 0.0032482
64974.3296 | 0.002017 | 64974.3296 | 0.002017 | 64974.3296 | 0.0032482
64985.9626 | 0.0020181 | 64985.9626 | 0.0020181 | 64985.9626 | 0.0032482
65006.8826 | 0.0020205 | 65006.8826 | 0.0020205 | 65006.8826 | 0.0032482
65034.7436 | 0.0020239 | 65034.7436 | 0.0020239 | 65034.7436 | 0.0032482
65070.1646 | 0.0020284 | 65070.1646 | 0.0020284 | 65070.1646 | 0.0032482
65121.9377 | 0.0020351 | 65121.9377 | 0.0020351 | 65121.9377 | 0.0032482
65213.3087 | 0.002047 | 65213.3087 | 0.002047 | 65213.3087 | 0.0032482
65373.5648 | 0.0020681 | 65373.5648 | 0.0020681 | 65373.5648 | 0.0032482
65606.9541 | 0.0020991 | 65606.9541 | 0.0020991 | 65606.9541 | 0.0032482
65931.838 | 0.0021426 | 65931.838 | 0.0021426 | 65931.838 | 0.0032482
66420.3992 | 0.0022081 | 66420.3992 | 0.0022081 | 66420.3992 | 0.0032482
67178.6066 | 0.0023102 | 67178.6066 | 0.0023102 | 67178.6066 | 0.0032482
67537.7005 | 0.0023586 | 67537.7005 | 0.0023586 | 67537.7005 | 0.0032482
67577.8755 | 0.002364 | 67577.8755 | 0.002364 | 67577.8755 | 0.0032482
67594.6742 | 0.0023663 | 67594.6742 | 0.0023663 | 67594.6742 | 0.0032482
67596.3462 | 0.0023665 | 67596.3462 | 0.0023665 | 67596.3462 | 0.0032482
67602.4792 | 0.0023673 | 67602.4792 | 0.0023673 | 67602.4792 | 0.0032482
67615.4987 | 0.0023691 | 67615.4987 | 0.0023691 | 67615.4987 | 0.0032482
67638.0448 | 0.0023721 | 67638.0448 | 0.0023721 | 67638.0448 | 0.0032482
67672.4794 | 0.0023767 | 67672.4794 | 0.0023767 | 67672.4794 | 0.0032482
67737.5261 | 0.0023855 | 67737.5261 | 0.0023855 | 67737.5261 | 0.0032482
67868.9209 | 0.0024032 | 67868.9209 | 0.0024032 | 67868.9209 | 0.0032482
68123.8552 | 0.0024376 | 68123.8552 | 0.0024376 | 68123.8552 | 0.0032482
68305.4351 | 0.002462 | 68305.4351 | 0.002462 | 68305.4351 | 0.0032482
68396.0464 | 0.0024742 | 68396.0464 | 0.0024742 | 68396.0464 | 0.0032482
68419.7504 | 0.0024743 | 68419.7504 | 0.0024743 | 68419.7504 | 0.0032482
68443.4544 | 0.0024729 | 68443.4544 | 0.0024729 | 68443.4544 | 0.0032482
68467.1584 | 0.0024712 | 68467.1584 | 0.0024712 | 68467.1584 | 0.0032482
68499.7608 | 0.002469 | 68499.7608 | 0.002469 | 68499.7608 | 0.0032482
68552.5634 | 0.0024656 | 68552.5634 | 0.0024656 | 68552.5634 | 0.0032482
68675.3717 | 0.0024575 | 68675.3717 | 0.0024575 | 68675.3717 | 0.0032482
68921.1348 | 0.0024413 | 68921.1348 | 0.0024413 | 68921.1348 | 0.0032482
69320.5028 | 0.0024152 | 69320.5028 | 0.0024152 | 69320.5028 | 0.0032482
69880.3274 | 0.0023787 | 69880.3274 | 0.0023787 | 69880.3274 | 0.0032482
70048.6371 | 0.0023678 | 70048.6371 | 0.0023678 | 70048.6371 | 0.0032482
70092.5451 | 0.002365 | 70092.5451 | 0.002365 | 70092.5451 | 0.0032482
70239.2697 | 0.0023555 | 70239.2697 | 0.0023555 | 70239.2697 | 0.0032482
70406.415 | 0.0023447 | 70406.415 | 0.0023447 | 70406.415 | 0.0032482
70573.5603 | 0.0023339 | 70573.5603 | 0.0023339 | 70573.5603 | 0.0032482
70986.2055 | 0.0023073 | 70986.2055 | 0.0023073 | 70986.2055 | 0.0032482
71575.101 | 0.0022696 | 71575.101 | 0.0022696 | 71575.101 | 0.0032482
72040.6257 | 0.0022421 | 72040.6257 | 0.0022421 | 72040.6257 | 0.0032482
72097.9244 | 0.0022413 | 72097.9244 | 0.0022413 | 72097.9244 | 0.0032482
72145.2566 | 0.0022409 | 72145.2566 | 0.0022409 | 72145.2566 | 0.0032482
72192.5889 | 0.0022405 | 72192.5889 | 0.0022405 | 72192.5889 | 0.0032482
72279.2219 | 0.0022397 | 72279.2219 | 0.0022397 | 72279.2219 | 0.0032482
72459.7094 | 0.0022381 | 72459.7094 | 0.0022381 | 72459.7094 | 0.0032482
72843.3171 | 0.0022346 | 72843.3171 | 0.0022346 | 72843.3171 | 0.0032482
73597.6988 | 0.0022278 | 73597.6988 | 0.0022278 | 73597.6988 | 0.0032482
74864.63 | 0.0022165 | 74864.63 | 0.0022165 | 74864.63 | 0.0032482
75669.4827 | 0.0022104 | 75669.4827 | 0.0022104 | 75669.4827 | 0.0032482
75843.7832 | 0.0022115 | 75843.7832 | 0.0022115 | 75843.7832 | 0.0032482
76018.0838 | 0.0022126 | 76018.0838 | 0.0022126 | 76018.0838 | 0.0032482
76192.3843 | 0.0022138 | 76192.3843 | 0.0022138 | 76192.3843 | 0.0032482
76627.8376 | 0.0022166 | 76627.8376 | 0.0022166 | 76627.8376 | 0.0032482
77714.1476 | 0.0022237 | 77714.1476 | 0.0022237 | 77714.1476 | 0.0032482
79442.1476 | 0.0022367 | 79442.1476 | 0.0022367 | 79442.1476 | 0.0032482
79844.9313 | 0.0022423 | 79844.9313 | 0.0022423 | 79844.9313 | 0.0032482
80247.715 | 0.002248 | 80247.715 | 0.002248 | 80247.715 | 0.0032482
80650.4988 | 0.0022537 | 80650.4988 | 0.0022537 | 80650.4988 | 0.0032482
81906.2025 | 0.0022712 | 81906.2025 | 0.0022712 | 81906.2025 | 0.0032482
83054.5058 | 0.0022871 | 83054.5058 | 0.0022871 | 83054.5058 | 0.0032482
83932.1531 | 0.0022991 | 83932.1531 | 0.0022991 | 83932.1531 | 0.0032482
84809.8004 | 0.0023109 | 84809.8004 | 0.0023109 | 84809.8004 | 0.0032482
85452.0733 | 0.0023196 | 85452.0733 | 0.0023196 | 85452.0733 | 0.0032482
86094.3462 | 0.0023281 | 86094.3462 | 0.0023281 | 86094.3462 | 0.0032482
86400 | 0.0023322 | 86400 | 0.0023322 | 86400 | 0.0032482